## INDEX
GUJARAT SLDC – SCED/SCUC MODEL DATA COMPENDIUM
Sheet | Contents | Source | Data Date | Status | Notes
1_INSTALLED_CAP | Installed & derated capacity of all generators | GETCO/SLDC PDF | 31-Dec-2025 | ✅ Complete | GSECL + IPP + Central sector GUVNL share
2_TECH_MINIMUM | Unit-wise technical minimum (Pmin) in MW | SLDC Technical Min PDF | Current | ✅ Complete | Coal & Gas units; hydro/RE excluded
3_MERIT_ORDER_VAR | Merit order – variable cost only (Rs/kWh) | SLDC MOD PDF 02-Jun-2026 | 02-Jun-2026 | ✅ Complete | 71 generators ranked
4_MERIT_ORDER_FULL | Full merit order with fixed + total cost + schedule | SLDC MOS Excel GJT | 30-May to 03-Jun-2026 | ✅ Complete | From MOSLDC Excel – 96+ entries with DC/Schedule
5_COAL_SUPPLY_CURVE | India coal power supply curve 2024-25 | ICED CSV 2024-25 | 2024-25 | ✅ Complete (Gujarat subset highlighted) | 153 plants all-India; 11 Gujarat plants
6_RAMP_RATES | Unit-wise ramp rates (MW/min) – CEA standard proxy | CEA/POSOCO standards | CERC Dec-2023 | ⚠️ Proxy | No Gujarat-specific data; using regulatory bands
7_MISSING_DATA | Data gaps to be sourced from SLDC/GETCO internally | — | — | ❌ Missing | Transmission network, load forecast, RE profile etc.
8_GUJ_ACTUAL_GEN | Gujarat station-wise actual generation (all fuels) – peak, off-peak, day energy | WRLDC PSP Report | 30-May-2026 | ✅ Complete | 29 stations incl wind/solar
9_ISGS_DRAWAL | Central sector ISGS actual generation + Gujarat allocated share | WRLDC PSP Report | 30-May-2026 | ✅ Complete | 25 ISGS stations
10_GUJ_DEMAND_CURT | Gujarat demand profile + generation mix % + RE curtailment data | WRLDC PSP Report | 30-May-2026 | ✅ Complete | ⚠️ Solar 1,684 MW + Wind 554 MW curtailed
11_RESERVOIR_LEVELS | Reservoir levels (SSP, Ukai, Kadana) present vs last year energy | WRLDC PSP Report | 30-May-2026 | ✅ Complete | Hydro constraint data now partially available
12_IR_EXCHANGE | WR inter-regional schedule; Gujarat market-wise drawal; frequency profile | WRLDC PSP Report | 30-May-2026 | ✅ Complete | ATC context + frequency deviation data
13_NETWORK_TOPOLOGY | Bus/substation list with voltage, zone, connected generators (50+ buses) | GETCO Power Map | 01-Sep-2023 | ⚠️ Topology only | R/X/B impedance + MVA limits still needed from GETCO
14_TRANSMISSION_LINES | Transmission line connectivity: 765/400/220kV + HVDC (60+ lines) | GETCO Power Map | 01-Sep-2023 | ⚠️ Topology only | Lengths and circuits identified; impedances UNKNOWN
15_ZONAL_MODEL | 5-zone model for GAMS: zone definitions, gen capacity per zone, 9 inter-zonal corridors | Derived from Power Map | 01-Sep-2023 | ✅ Ready for GAMS | Transfer limits indicative; confirm with GETCO ATC
16_CEA_OPERATION_NORMS | CEA normative heat rates, FOR%, MUT/MDT, APC for all technology types | CEA Recommendations CERC 2024-29 | 2024 | ✅ Complete | Ready for GAMS parameterisation
17_GETCO_SUBSTATION_LIST | 77 GETCO 220/132kV substations by zone, circle, district | GETCO Annexure-A (Scribd) | 2016 | ⚠️ Needs update | Supplements Sheet 13 bus list
18_OUTAGE_FRAMEWORK | Unit-wise normative FOR%, PAF%, availability parameter for GAMS; NPP download guide | CEA/NPP npp.gov.in | Daily (manual) | ⚠️ Proxy/Framework | Download DGR-10 XLS daily from NPP
19_SPINNING_RESERVE | Spinning reserve & ancillary service framework; GERC BESS 2026; IEGC FRO | GERC BESS Reg 2026 + CERC AS Reg | May-2026 | ⚠️ Framework | Exact MW quantum needs SLDC confirmation
20_DATA_SOURCES_REGISTER | Master register of all 25 data sources — status, URL, access method, sheet mapping | Compiled | Jun-2026 | ✅ Complete | Use as data management reference
DATA AUTHENTICITY: 🟢 AUTH = Official source / uploaded doc ¦ 🟡 DERIV = Calculated from authentic data ¦ 🟠 PROXY = Regulatory norm (CEA/CERC/IEA) — valid but not unit-specific ¦ 🔴 REPR = Reproduced by engineering judgment — MUST BE VERIFIED before GAMS use
21_LOAD_PROFILE_96BLK | 96-block load profile — 4 seasons × weekday/weekend + solar/wind/residual | 🔴 REPR (shape) + 🟢 AUTH anchors | WRLDC PSP 30-May-2026 | ⚠️ Estimated | 3 AUTH anchor blocks (peak/trough/max). Verify full profile with SLDC.
22_RE_GEN_PROFILE | 96-block RE profile — total + 4-zone solar split + 2-zone wind split | 🔴 REPR (shape) + 🟢 AUTH anchors | WRLDC PSP 30-May-2026 | ⚠️ Estimated | AUTH anchors at solar peak 12:08 and wind peak 20:06. Verify with SLDC REMC.
23_LINE_IMPEDANCES | R/X/B per-unit + Smax for 59 lines (765/400/220kV + HVDC); 100 MVA base | 🟠 PROXY — standard ACSR params × map lengths | CEA/IEEE standards | ⚠️ Proxy | MUST replace with GETCO actual impedances for security-constrained model.
24_STARTUP_COSTS | UC parameters: no-load cost, cold/warm/hot startup cost, MUT/MDT for 36 units | 🟠 PROXY (fixed cost, MUT) + 🔴 REPR (startup cost formula) | CERC/CEA 2024 | ⚠️ Proxy+Repr | VC from merit order (🟢AUTH). Startup = Pmin×MUT×VC + oil cost formula.
25_GAS_NOMINATIONS | Gas tier structure (APM/RLNG/Spot) + prices + estimated daily volumes for 10 plants | 🟢 AUTH (prices from MO PDF) + 🔴 REPR (volumes) | SLDC MO PDF 02-Jun-2026 | ⚠️ Partial | Prices authentic. Volumes estimated from Pmin×HR/HV. Get actuals from GAIL/GSPC.

## 1_INSTALLED_CAP
GUJARAT – INSTALLED & DERATED CAPACITY ¦ Source: GETCO/SLDC ¦ Date: 31-Dec-2025
# | Generator / Station | Sector | Fuel Type | Ownership | Installed Cap (MW) | Derated / GUVNL Share (MW) | % Share (GUVNL) | Remarks | Data Source
1 | DHUVARAN CCPP | GSECL | Gas | GSECL | 595.1 | 488.1 |  | Incl GT1-4 + STG 1-3 | Installed Cap PDF
2 | UKAI TPS | GSECL | Coal | GSECL | 1110 | 1110 |  | Units 1-6 | Installed Cap PDF
3 | GANDHINAGAR TPS | GSECL | Coal | GSECL | 630 | 630 |  | Units 3-5 (1&2 retired) | Installed Cap PDF
4 | WANAKBORI TPS | GSECL | Coal | GSECL | 2270 | 2270 |  | Units 1-8 | Installed Cap PDF
5 | SIKKA TPS | GSECL | Coal | GSECL | 500 | 500 |  | Units 3-4 | Installed Cap PDF
6 | PANANDHRO | GSECL | Coal/Lignite | GSECL | 150 | 150 |  |  | Installed Cap PDF
7 | BECL | GSECL | Coal | GSECL | 500 | 500 |  |  | Installed Cap PDF
8 | UTRAN-II CCPP | GSECL | Gas | GSECL | 375 | 374.57 |  |  | Installed Cap PDF
9 | UKAI HYDRO | GSECL | Hydro | GSECL | 305 | 305 |  |  | Installed Cap PDF
10 | KADANA HYDRO | GSECL | Hydro | GSECL | 242 | 242 |  |  | Installed Cap PDF
11 | TP-AECO (AMGEN) | IPP/PVT | Coal | IPP | 362 | 362 |  |  | Installed Cap PDF
12 | GIPCL-I (MANGROL) | IPP/PVT | Gas/Lignite | GIPCL | 145 | 93 |  |  | Installed Cap PDF
13 | SLPP (GIPCL) | IPP/PVT | Lignite | GIPCL | 500 | 500 |  | 4×125 MW | Installed Cap PDF
14 | GSEG-II (GSPC) | IPP/PVT | Gas | GSPC | 351 | 351 |  |  | Installed Cap PDF
15 | EPGL (Essar) | IPP/PVT | Coal | Essar | 1200 | 1122 |  | 2×600 MW | Installed Cap PDF
16 | AKRIMOTA (BECL) | IPP/PVT | Lignite | BECL | 250 | 250 |  | 2×125 MW | Installed Cap PDF
17 | SUGEN CCPP | IPP/PVT | Gas | Torrent | 1148 | 1148 |  |  | Installed Cap PDF
18 | UNOSUGEN | IPP/PVT | Gas | Torrent | 383 | 383 |  |  | Installed Cap PDF
19 | APL (Adani Mundra) | IPP/PVT | Coal | Adani | 2640 | 2434 |  | Stage 1: 4×330 + Stage 2: 2×660 | Installed Cap PDF
20 | ACB India Ltd | IPP/PVT | Coal | ACB | 270 | 200 |  |  | Installed Cap PDF
21 | GSPC PIPAVAV (CLPI) | IPP/PVT | Gas | GSPC | 702.86 | 703 |  |  | Installed Cap PDF
22 | OPGS | IPP/PVT | Gas | OPGS | 300 | 0 |  | Currently 0 MW | Installed Cap PDF
23 | DB Power | IPP/PVT | Coal | DB Power | 293 | 293 |  |  | Installed Cap PDF
24 | KAKRAPAR (KAPS 1&2) | Central | Nuclear | NPCIL | 440 | 125 | 28.41% | GUVNL share | Installed Cap PDF
25 | KAKRAPAR EXT (3&4) | Central | Nuclear | NPCIL | 700 | 475.88 | 33.99% | GUVNL share | Installed Cap PDF
26 | TARAPUR 1&2 | Central | Nuclear | NPCIL | 320 | 160 | 50.00% | GUVNL share | Installed Cap PDF
27 | TARAPUR 3&4 | Central | Nuclear | NPCIL | 1080 | 274 | 25.37% | GUVNL share | Installed Cap PDF
28 | KORBA (NTPC) | Central | Coal | NTPC | 2100 | 380.84 | 18.14% | GUVNL share | Installed Cap PDF
29 | KORBA-7 (NTPC) | Central | Coal | NTPC | 500 | 130.34 | 26.07% | GUVNL share | Installed Cap PDF
30 | VSTPS-I | Central | Coal | NTPC | 1260 | 247.74 | 19.66% | GUVNL share | Installed Cap PDF
31 | VSTPS-II | Central | Coal | NTPC | 1000 | 252.64 | 25.26% | GUVNL share | Installed Cap PDF
32 | VSTPS-III | Central | Coal | NTPC | 1000 | 279.64 | 27.96% | GUVNL share | Installed Cap PDF
33 | VSTPS-IV | Central | Coal | NTPC | 1000 | 258.6 | 25.86% | GUVNL share | Installed Cap PDF
34 | VSTPS-V | Central | Coal | NTPC | 500 | 102.79 | 20.56% | GUVNL share | Installed Cap PDF
35 | JHANOR-JGPS (KAWAS) | Central | Gas | NTPC | 657.4 | 237 | 36.05% | GUVNL share | Installed Cap PDF
36 | KAWAS GAS | Central | Gas | NTPC | 656.2 | 187 | 28.50% | GUVNL share | Installed Cap PDF
37 | SIPAT-I | Central | Coal | NTPC | 1980 | 576.99 | 29.14% | GUVNL share | Installed Cap PDF
38 | SIPAT-II | Central | Coal | NTPC | 1000 | 286.02 | 28.60% | GUVNL share | Installed Cap PDF
39 | GADARWARA-I | Central | Coal | NTPC | 1600 | 333.83 | 20.86% | GUVNL share | Installed Cap PDF
40 | CGPL MUNDRA UMPP | Central | Coal | Tata | 4150 | 1805 | 47.50% | *Ex-Bus 3800 MW basis | Installed Cap PDF
41 | MSTPS-I (MAUDA) | Central | Coal | NTPC | 1000 | 455.633 | 45.56% | GUVNL share | Installed Cap PDF
42 | MSTPS-II (MAUDA) | Central | Coal | NTPC | 1320 | 530.243 | 40.17% | GUVNL share | Installed Cap PDF
43 | LARA STPP | Central | Coal | NTPC | 1600 | 186.478 | 11.65% | GUVNL share | Installed Cap PDF
44 | KHARGONE STPS | Central | Coal | NTPC | 1320 | 270.197 | 20.47% | GUVNL share | Installed Cap PDF
45 | DADRI-I | Central | Coal | NTPC | 840 | 576.996 | 68.69% | GUVNL share | Installed Cap PDF
46 | SSP-CHPH | Central | Hydro | SSNNL | 250 | 40 | 16.00% | GUVNL share | Installed Cap PDF
47 | SSP-RBPH | Central | Hydro | SSNNL | 1200 | 192 | 16.00% | GUVNL share | Installed Cap PDF
48 | WIND (incl. Hybrid) | RE | Wind | Various | 8849.885 | 8849.885 |  | As on 31-Dec-2025 | Installed Cap PDF
49 | SOLAR (excl. Rooftop) | RE | Solar | Various | 17971.259 | 17971.259 |  | Incl Raghanesda & SKY | Installed Cap PDF
50 | KURNOOL3 SOLAR RE | RE | Solar | Various | 255.9 | 255.9 |  |  | Installed Cap PDF
51 | BIOMASS | RE | Biomass | Various | 81.65 | 81.65 |  |  | Installed Cap PDF
TOTAL GUJARAT (incl Wind/Solar/Biomass/Small Hydro) |  |  |  |  | 69854.254 | 49932.221

## 2_TECH_MINIMUM
UNIT-WISE TECHNICAL MINIMUM (Pmin) ¦ Source: SLDC Vadodara Technical Minimum PDF ¦ Date: Current
# | Station / Unit | Unit No. | Installed Cap (MW) | Tech Min / Pmin (MW) | Config Note | Fuel | Source
1 | SIKKA | 1 | 120 | 75.65 |  | Coal | Tech Min PDF
2 | SIKKA | 2 | 120 | 80.1 |  | Coal | Tech Min PDF
3 | SIKKA | 3 | 250 | 165 |  | Coal | Tech Min PDF
4 | KLTPS | 1 | 70 | 39.488 |  | Coal | Tech Min PDF
5 | KLTPS | 2 | 70 | 39.488 |  | Coal | Tech Min PDF
6 | KLTPS | 3 | 75 | 43.875 |  | Coal | Tech Min PDF
7 | KLTPS | 4 | 75 | 43.88 |  | Coal | Tech Min PDF
8 | GANDHINAGAR | 1 | 120 | 62 |  | Coal | Tech Min PDF
9 | GANDHINAGAR | 2 | 120 | 62 |  | Coal | Tech Min PDF
10 | GANDHINAGAR | 3 | 210 | 141 |  | Coal | Tech Min PDF
11 | GANDHINAGAR | 4 | 210 | 141 |  | Coal | Tech Min PDF
12 | GANDHINAGAR | 5 | 210 | 154 | Unit 5 separate | Coal | Tech Min PDF
13 | UKAI TPS | 1 | 120 | 62 |  | Coal | Tech Min PDF
14 | UKAI TPS | 2 | 120 | 61.5 |  | Coal | Tech Min PDF
15 | UKAI TPS | 3 | 200 | 135 |  | Coal | Tech Min PDF
16 | UKAI TPS | 4 | 200 | 135 |  | Coal | Tech Min PDF
17 | UKAI TPS | 5 | 210 | 150.5 |  | Coal | Tech Min PDF
18 | UKAI TPS | 6 | 500 | 336.6 |  | Coal | Tech Min PDF
19 | WANAKBORI | 1 | 210 | 144.8 |  | Coal | Tech Min PDF
20 | WANAKBORI | 2 | 210 | 144.8 |  | Coal | Tech Min PDF
21 | WANAKBORI | 3 | 210 | 144.8 |  | Coal | Tech Min PDF
22 | WANAKBORI | 4 | 210 | 144.8 |  | Coal | Tech Min PDF
23 | WANAKBORI | 5 | 210 | 144.8 |  | Coal | Tech Min PDF
24 | WANAKBORI | 6 | 210 | 144.8 |  | Coal | Tech Min PDF
25 | WANAKBORI | 7 | 210 | 144.8 |  | Coal | Tech Min PDF
26 | UTRAN CCPP | 1 GT+STG | 30 | 30 | 30 MW with 1 GT+STG | Gas | Tech Min PDF
27 | UTRAN CCPP | 2 GT+STG | 30 | 65 | 65 MW with 2 GT+STG | Gas | Tech Min PDF
28 | UTRAN CCPP | 3 GT+STG | 30 | 103 | 103 MW with 3 GT+STG | Gas | Tech Min PDF
29 | UTRAN CCPP | STG | 45 | — |  | Gas | Tech Min PDF
30 | DGBPS-1 (Dhuvaran) | GT | 67.85 | N/A |  | Gas | Tech Min PDF
31 | DGBPS-1 (Dhuvaran) | STG | 38.77 | N/A |  | Gas | Tech Min PDF
32 | DGBPS-2 (Dhuvaran) | GT | 72.51 | N/A |  | Gas | Tech Min PDF
33 | DGBPS-2 (Dhuvaran) | STG | 39.94 | N/A |  | Gas | Tech Min PDF
34 | UGPP-II (Unosugen) | GT | 228 | 69 | Min 69 MW (1GT+STG) | Gas | Tech Min PDF
35 | UGPP-II (Unosugen) | GT+STG | — | 73 | Min 73 MW | Gas | Tech Min PDF
36 | UGPP-II (Unosugen) | Full | 374 | 188 | Full config | Gas | Tech Min PDF
37 | GSEG | GT-1+STG | 52 | 51 | 51 MW with 1 GT+STG | Gas | Tech Min PDF
38 | GSEG | GT-2+STG | 52 | 101 | 101 MW with 2 GT+STG | Gas | Tech Min PDF
39 | GSEG | STG | 52 | — |  | Gas | Tech Min PDF
40 | CLPI (GSPC Pipavav) | 1 GT+STG | 138 | 142 | 142 MW with 1 GT | Gas | Tech Min PDF
41 | CLPI (GSPC Pipavav) | 2 GT+STG | 138 | 284 | 284 MW with 2 GT | Gas | Tech Min PDF
42 | CLPI (GSPC Pipavav) | 3 GT+STG | 138 | 426 | 426 MW with 3 GT | Gas | Tech Min PDF
43 | CLPI (GSPC Pipavav) | STG | 241 | — |  | Gas | Tech Min PDF
44 | SLPP (GIPCL) | 1 | 125 | 60 |  | Lignite | Tech Min PDF
45 | SLPP (GIPCL) | 2 | 125 | 60 |  | Lignite | Tech Min PDF
46 | SLPP (GIPCL) | 3 | 125 | 60 |  | Lignite | Tech Min PDF
47 | SLPP (GIPCL) | 4 | 125 | 60 |  | Lignite | Tech Min PDF
48 | GIPCL-I | 1 GT+STG | 32 | 35 | 35 MW with 1 GT+STG | Gas | Tech Min PDF
49 | GIPCL-I | 2 GT+STG | 32 | 65 | 65 MW with 2 GT+STG | Gas | Tech Min PDF
50 | GIPCL-I | 3 GT+STG | 32 | 105 | 105 MW with 3 GT+STG | Gas | Tech Min PDF
51 | GIPCL-I | STG | 49 | — |  | Gas | Tech Min PDF
52 | GIPCL-II | GT | 110.4 | N/A |  | Gas | Tech Min PDF
53 | GIPCL-II | STG | 54.6 | N/A |  | Gas | Tech Min PDF
54 | AKRIMOTA (BECL) | 1 | 125 | 50 |  | Lignite | Tech Min PDF
55 | AKRIMOTA (BECL) | 2 | 125 | 50 |  | Lignite | Tech Min PDF
56 | ADANI MUNDRA Stage-1 | 1 | 330 | 200 |  | Coal | Tech Min PDF
57 | ADANI MUNDRA Stage-1 | 2 | 330 | 200 |  | Coal | Tech Min PDF
58 | ADANI MUNDRA Stage-1 | 3 | 330 | 200 |  | Coal | Tech Min PDF
59 | ADANI MUNDRA Stage-1 | 4 | 330 | 200 |  | Coal | Tech Min PDF
60 | ADANI MUNDRA Stage-2 | 1 | 660 | 400 |  | Coal | Tech Min PDF
61 | ADANI MUNDRA Stage-2 | 2 | 660 | 400 |  | Coal | Tech Min PDF
62 | EPGL (Essar) | 1 | 600 | 360 |  | Coal | Tech Min PDF
63 | EPGL (Essar) | 2 | 600 | 360 |  | Coal | Tech Min PDF

## 3_MERIT_ORDER_VAR
MERIT ORDER – VARIABLE COST BASIS ¦ Source: SLDC Merit Order PDF ¦ Date: 02-Jun-2026
Rank | Generator / Station | Variable Cost (Rs/kWh) | Delivery Point | Fuel Type | Source Doc | Notes
1 | SARDAR SAROVAR PROJECT | 2.05 | GETCO periphery | Hydro | MOD PDF 02-Jun-26 | Compulsory share
2 | KAKRAPAR APS (KAPS 1&2) | 2.29 | GETCO periphery | Nuclear | MOD PDF 02-Jun-26 | Compulsory share
3 | TARAPUR APS 1&2 | 2.42 | GETCO periphery | Nuclear | MOD PDF 02-Jun-26 | Compulsory share
4 | TARAPUR APS 3&4 | 3.65 | GETCO periphery | Nuclear | MOD PDF 02-Jun-26 | Compulsory share
5 | KAKRAPAR EXT (3&4) | 4.4 | GETCO periphery | Nuclear | MOD PDF 02-Jun-26 | Compulsory share
6 | ACB India Ltd | 1.09 | GETCO periphery | Coal | MOD PDF 02-Jun-26
7 | SIPAT-1 | 1.27 | GETCO periphery | Coal | MOD PDF 02-Jun-26
8 | LARA STPS | 1.31 | GETCO periphery | Coal | MOD PDF 02-Jun-26
9 | SIPAT-2 | 1.31 | GETCO periphery | Coal | MOD PDF 02-Jun-26
10 | KORBA-III | 1.37 | GETCO periphery | Coal | MOD PDF 02-Jun-26
11 | KORBA I&II | 1.39 | GETCO periphery | Coal | MOD PDF 02-Jun-26
12 | DB POWER LIMITED | 1.56 | GETCO periphery | Coal | MOD PDF 02-Jun-26
13 | VINDHYACHAL STAGE-4 | 2.1 | GETCO periphery | Coal | MOD PDF 02-Jun-26
14 | VINDHYACHAL STAGE-3 | 2.12 | GETCO periphery | Coal | MOD PDF 02-Jun-26
15 | VINDHYACHAL STAGE-2 | 2.14 | GETCO periphery | Coal | MOD PDF 02-Jun-26
16 | VINDHYACHAL STAGE-5 | 2.16 | GETCO periphery | Coal | MOD PDF 02-Jun-26
17 | VINDHYACHAL STAGE-1 | 2.23 | GETCO periphery | Coal | MOD PDF 02-Jun-26
18 | AKRIMOTA | 2.84 | State bus | Lignite | MOD PDF 02-Jun-26
19 | BARH-I | 2.86 | GETCO periphery | Coal | MOD PDF 02-Jun-26
20 | KAHALGAON-2 | 2.98 | GETCO periphery | Coal | MOD PDF 02-Jun-26
21 | NABINAGAR STPP | 3.01 | GETCO periphery | Coal | MOD PDF 02-Jun-26
22 | MAUDA STPS-II | 3.15 | GETCO periphery | Coal | MOD PDF 02-Jun-26
23 | KAHALGAON-1 | 3.19 | GETCO periphery | Coal | MOD PDF 02-Jun-26
24 | MAUDA STPS-I | 3.19 | GETCO periphery | Coal | MOD PDF 02-Jun-26
25 | GADARWARA STPS | 3.24 | GETCO periphery | Coal | MOD PDF 02-Jun-26
26 | GIPCL MANGROL SLPP | 3.36 | State bus | Lignite | MOD PDF 02-Jun-26
27 | FARAKKA-3 | 3.37 | GETCO periphery | Coal | MOD PDF 02-Jun-26
28 | KHARGONE STPS | 3.41 | GETCO periphery | Coal | MOD PDF 02-Jun-26
29 | FARAKKA 1&2 | 3.44 | GETCO periphery | Coal | MOD PDF 02-Jun-26
30 | GIPCL SLPP EXPANSION | 3.45 | State bus | Lignite | MOD PDF 02-Jun-26
31 | UNCHAHAR-I | 3.67 | GETCO periphery | Coal | MOD PDF 02-Jun-26
32 | SOLAPUR TPS | 4.19 | GETCO periphery | Coal | MOD PDF 02-Jun-26
33 | BLTPS 1&2 (BECL) | 4.23 | State bus | Lignite | MOD PDF 02-Jun-26
34 | DADRI-I | 4.26 | GETCO periphery | Coal | MOD PDF 02-Jun-26
35 | WANAKBORI TPS-8 | 4.41 | State bus | Coal | MOD PDF 02-Jun-26
36 | UKAI TPS-6 | 4.51 | State bus | Coal | MOD PDF 02-Jun-26
37 | CGPL MUNDRA UMPP | 4.6 | GETCO periphery | Coal | MOD PDF 02-Jun-26 | Imported coal
38 | UKAI TPS-4 | 4.7 | State bus | Coal | MOD PDF 02-Jun-26
39 | KLTPS-3 | 4.73 | State bus | Coal | MOD PDF 02-Jun-26
40 | APL-II (Adani Mundra) Stg-2 | 4.82 | State bus | Coal | MOD PDF 02-Jun-26 | As conveyed by APMuL
41 | KLTPS-4 | 4.82 | State bus | Coal | MOD PDF 02-Jun-26
42 | APL-II (200 MW block) | 4.83 | State bus | Coal | MOD PDF 02-Jun-26 | As conveyed by APMuL
43 | WANAKBORI TPS-3 | 4.83 | State bus | Coal | MOD PDF 02-Jun-26
44 | APL-I (Adani Mundra) Stg-1 | 5.16 | State bus | Coal | MOD PDF 02-Jun-26 | As conveyed by APMuL
45 | APL-I (200 MW block) | 5.17 | State bus | Coal | MOD PDF 02-Jun-26 | As conveyed by APMuL
46 | GANDHINAGAR TPS Unit-5 | 5.18 | State bus | Coal | MOD PDF 02-Jun-26
47 | WANAKBORI TPS Unit-7 | 5.18 | State bus | Coal | MOD PDF 02-Jun-26
48 | WANAKBORI TPS Units 1,2,4,5,6 | 5.23 | State bus | Coal | MOD PDF 02-Jun-26
49 | UKAI TPS 3&5 | 5.35 | State bus | Coal | MOD PDF 02-Jun-26
50 | GANDHINAGAR TPS Units 3,4 | 5.39 | State bus | Coal | MOD PDF 02-Jun-26
51 | EPGL (Essar Power Gujarat) | 5.52 | State bus | Coal | MOD PDF 02-Jun-26
52 | SIKKA 3-4 | 6.1 | State bus | Coal | MOD PDF 02-Jun-26
53 | JHANOR-JGPS APM | 7.25 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | APM gas
54 | KAWAS GAS APM | 7.28 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | APM gas
55 | JHANOR-JGPS NON-APM | 7.39 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | Non-APM gas
56 | KAWAS GAS NON-APM | 7.42 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | Non-APM gas
57 | KAWAS RLNG | 9.52 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | RLNG
58 | JHANOR RLNG | 10.04 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | RLNG
59 | GSEG EXPANSION High Sea Gas | 10.3 | State bus | Gas | MOD PDF 02-Jun-26 | High Sea Gas
60 | GPPC High Sea Gas | 11.89 | State bus | Gas | MOD PDF 02-Jun-26 | High Sea Gas
61 | UTRAN-II High Sea Gas | 12.73 | State bus | Gas | MOD PDF 02-Jun-26 | High Sea Gas
62 | DHUVARAN CCPP-III High Sea Gas | 13.08 | State bus | Gas | MOD PDF 02-Jun-26 | High Sea Gas
63 | DHUVARAN CCPP-II High Sea Gas | 14.36 | State bus | Gas | MOD PDF 02-Jun-26 | High Sea Gas
64 | GSEG EXPANSION GSPC Spot Gas | 15.1 | State bus | Gas | MOD PDF 02-Jun-26 | Spot gas
65 | DHUVARAN CCPP-III GSPC Spot | 15.1 | State bus | Gas | MOD PDF 02-Jun-26 | Spot gas
66 | UTRAN-II GSPC Spot Gas | 15.1 | State bus | Gas | MOD PDF 02-Jun-26 | Spot gas
67 | KAWAS GAS Comm | 15.56 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | Commercial RLNG
68 | GPPC GSPC Spot Gas | 15.6 | State bus | Gas | MOD PDF 02-Jun-26 | Spot gas
69 | JHANOR-JGPS Comm | 15.69 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | Commercial RLNG
70 | DHUVARAN CCPP-II GSPC Spot | 17.45 | State bus | Gas | MOD PDF 02-Jun-26 | Spot gas
71 | KAWAS-KGPS Liquid | 25.11 | GETCO periphery | Gas | MOD PDF 02-Jun-26 | Liquid fuel

## 4_MERIT_ORDER_FULL
FULL MERIT ORDER WITH SCHEDULE ¦ Source: MeritOrderSummary_GJT Excel ¦ Period: 30-May to 03-Jun-2026
# | Station | Fuel Type | Ownership | Cap Allocated to State (MW) | Plant Capacity (MW) | Variable Cost (Rs/kWh) | Fixed Cost (Rs/kWh) | Total Cost (Rs/kWh) | Declared Capability (MWh) | Schedule (MWh) | Remarks / Must-Run
1 | GSEG_SPOT | Gas | State Gen | 156 | 156 | 0 | 0.46 | 0.46 | 76720 | 76720 | DC = TM / MUST RUN
2 | UGBPS_2 GAIL SPOT (Unosugen) | Gas | State Gen | 375 | 375 | 0 | 0 | 0 | 1752 | 1752 | DC = TM / MUST RUN
3 | KHPS (Kadana Hydro) | Hydro | State Gen | 240 | 240 | 0 | 1.07 | 1.07 | 523 | 522 | DC = TM / MUST RUN
4 | DHUVARAN CCPP-II ONGC WO | Gas | State Gen | 112 | 112 | 0 | 0.72 | 0.72 | 121168 | 121168 | DC = TM / MUST RUN
5 | TAPS 1&2 | Nuclear | Central ISGS | 160 | 320 | 2.42 | 0 | 2.42 | 1752 | 1752 | DC = TM / MUST RUN
6 | ACBIL | Coal | Other ISGS | 200 | 270 | 1.09 | 1.46 | 2.55 | 2658 | 2568
7 | DARLIPALLI-I | Coal | State Gen | 14 | 800 | 1.14 | 2.12 | 3.26 | 0 | 0
8 | LSTPP WR (Lara) | Coal | State Gen | 157 | 1600 | 1.16 | 1.8 | 2.96 | 2063 | 1557
9 | SIPAT-1 | Coal | Central ISGS | 509 | 1980 | 1.56 | 1.3 | 2.86 | 12880 | 9504
10 | SIPAT-2 WR | Coal | Central ISGS | 257 | 1000 | 1.63 | 1.24 | 2.87 | 6512 | 4806
11 | KSTPS 3 WR | Coal | Central ISGS | 90 | 500 | 1.67 | 0.69 | 2.36 | 2374 | 1685
12 | KSTPS WR (Korba) | Coal | Central ISGS | 336 | 2100 | 1.7 | 0.69 | 2.39 | 6546 | 4639
13 | TSTPS I ER (Telcher) | Coal | Central ISGS | 24 | 1000 | 1.71 | 0.96 | 2.67 | 0 | 0
14 | SSP (Sardar Sarovar) | Hydro | Other ISGS | 232 | 1450 | 2.05 | 0 | 2.05 | 1191 | 192
15 | VSTPS-3 | Coal | Central ISGS | 251 | 1000 | 2.17 | 1.05 | 3.22 | 6286 | 3989
16 | VSTPS-4 | Coal | Central ISGS | 226 | 1000 | 2.18 | 1.57 | 3.75 | 5771 | 3660
17 | VTPS-2 | Coal | Central ISGS | 225 | 1000 | 2.19 | 0.7 | 2.89 | 5633 | 3559
18 | VSTPS-5 | Coal | Central ISGS | 88 | 500 | 2.23 | 1.67 | 3.9 | 2287 | 1446
19 | VTPS-1 | Coal | Central ISGS | 209 | 1260 | 2.28 | 0.86 | 3.14 | 4518 | 2856
20 | KAPS (Kakrapar 1&2) | Nuclear | Central ISGS | 115 | 440 | 2.29 | 0 | 2.29 | 2714 | 2713
21 | AKRIMOTA ALTPS | Lignite | State Gen | 250 | 250 | 2.71 | 0.79 | 3.5 | 2760 | 2658
22 | NABINAGAR STPP | Coal | State Gen | 50 | 50 | 2.87 | 2.37 | 5.24 | 1141 | 711
23 | KAHALGAON-II | Coal | Central ISGS | 133 | 1500 | 2.93 | 1.05 | 3.98 | 3189 | 1954
24 | SLPP-II (GIPCL) | Lignite | State Gen | 250 | 250 | 2.94 | 1.53 | 4.47 | 5066 | 4332
25 | SLPP-1 (GIPCL) | Lignite | State Gen | 250 | 250 | 2.94 | 0.73 | 3.67 | 4243 | 3779
26 | BARH-I | Coal | State Gen | 139 | 139 | 2.97 | 2.42 | 5.39 | 3090 | 1951
27 | KSPP-I ER (Kahelgaon) | Coal | Central ISGS | 13 | 840 | 3.13 | 1.05 | 4.18 | 2097 | 1105
28 | MAUDA-II | Coal | Central ISGS | 138 | 1320 | 3.2 | 1.48 | 4.68 | 7100 | 3659
29 | TANDA II NR | Coal | Central ISGS | 44 | 660 | 3.21 | 1.6 | 4.81 | 0 | 0
30 | MAUDA-I | Coal | Central ISGS | 226 | 1000 | 3.22 | 1.88 | 5.1 | 5720 | 2932
31 | FSTPS-III ER (Farakka) | Coal | Central ISGS |  | 500 | 3.32 | 1.49 | 4.81 | 2482 | 1413
32 | GADARWARA-I | Coal | Central ISGS | 304 | 1600 | 3.41 | 2.08 | 5.49 | 7444 | 4434
33 | FSTPS I&II ER (Farakka) | Coal | Central ISGS | 26 | 1600 | 3.44 | 0.82 | 4.26 | 4742 | 2695
34 | AMGEN DEF (TP-AECO) | Coal | State Gen | 362 | 362 | 3.5 | 0 | 3.5 | 7804 | 6778
35 | TAPS 3&4 | Nuclear | Central ISGS | 249 | 1080 | 3.65 | 0 | 3.65 | 4719 | 4718
36 | UNCHAHAR-I NR | Coal | Central ISGS | 36 | 420 | 3.72 | 1.08 | 4.8 | 583 | 318
37 | CGPL MUNDRA UMPP | Coal | Other ISGS | 1805 | 4000 | 3.73 | 0.9 | 4.63 | 40167 | 29878
38 | UNO SUGEN | Gas | State Gen | 361 | 361 | 3.79 | 0 | 3.79 | 143 | 142 | DC = TM / MUST RUN
39 | KHARGONE STPS | Coal | Central ISGS | 246 | 1320 | 3.84 | 1.81 | 5.65 | 6025 | 3433
40 | BECL | Coal | State Gen | 500 | 500 | 4.1 | 2.63 | 6.73 | 5843 | 5517
41 | EPGL | Coal | State Gen | 1200 | 1200 | 4.1 | 1.09 | 5.19 | 26928 | 17354
42 | ADANI (Mundra) Unit 5-6 | Coal | State Gen | 1000 | 1320 | 4.16 | 1 | 5.16 | 21861 | 19633
43 | APMUL-2 Additional 234 | Coal | State Gen | 234 | 234 | 4.21 | 1 | 5.21 | 5116 | 1724
44 | WTPS-8 (Wanakbori) | Coal | State Gen | 800 | 800 | 4.32 | 0.75 | 5.07 | 18192 | 14712
45 | UTPS-6 (Ukai) | Coal | State Gen | 500 | 500 | 4.35 | 1.7 | 6.05 | 11280 | 9165
46 | ADANI (Mundra) Unit 1-4 | Coal | State Gen | 1000 | 1320 | 4.45 | 1.21 | 5.66 | 24000 | 16725
47 | KLTPS 1-3 | Coal | State Gen | 215 | 215 | 4.49 | 1.5 | 5.99 | 1392 | 1135
48 | APMUL-1 Additional 200 | Coal | State Gen | 200 | 200 | 4.5 | 1 | 5.5 | 4800 | 140
49 | UTPS-4 (Ukai) | Coal | State Gen | 200 | 200 | 4.56 | 0.38 | 4.94 | 4292 | 3394
50 | SOLAPUR | Coal | State Gen | 24 | 1320 | 4.57 | 1.72 | 6.29 | 530 | 291
51 | KLTPS-4 | Coal | State Gen | 75 | 75 | 4.82 | 1.95 | 6.77 | 0 | 0
52 | DADRI-I NR | Coal | State Gen | 577 | 577 | 4.86 | 0.97 | 5.83 | 12671 | 6095
53 | WTPS-3 (Wanakbori) | Coal | State Gen | 210 | 210 | 4.92 | 0.47 | 5.39 | 4586 | 3386
54 | SUGEN CCPP | Gas | State Gen | 1148 | 1148 | 4.94 | 0 | 4.94 | 6109 | 5543
55 | GTPS-5 (Gandhinagar) | Coal | State Gen | 210 | 210 | 5.15 | 0.63 | 5.78 | 0 | 0
56 | WTPS-7 (Wanakbori) | Coal | State Gen | 210 | 210 | 5.24 | 0.61 | 5.85 | 4561 | 2520
57 | WTPS 1-6 (Wanakbori) | Coal | State Gen | 1260 | 1260 | 5.28 | 0.47 | 5.75 | 0 | 0
58 | UTPS 1-5 (Ukai) | Coal | State Gen | 850 | 850 | 5.3 | 0.38 | 5.68 | 0 | 0
59 | GTPS 3-4 (Gandhinagar) | Coal | State Gen | 420 | 420 | 5.5 | 1.08 | 6.58
60 | GANDHAR GAS APM | Gas | Central ISGS | 231 | 657 | 5.88 | 1.06 | 6.94 | 0 | 0
61 | KAWAS GAS APM | Gas | Central ISGS | 182 | 656 | 5.91 | 0.84 | 6.75 | 0 | 0
62 | GANDHAR NAPM | Gas | Central ISGS | 231 | 657 | 6 | 1.06 | 7.06 | 0 | 0
63 | KAWAS NAPM | Gas | Central ISGS | 182 | 656 | 6.02 | 0.84 | 6.86 | 0 | 0
64 | SUGEN SPOT Gas | Gas | State Gen | 1148 | 1148 | 6.27 | 0 | 6.27 | 389 | 0
65 | STPS 3&4 (Sikka) | Coal | State Gen | 500 | 500 | 6.35 | 1.58 | 7.93 | 0 | 0
66 | GSEG-II High Sea Gas | Gas | State Gen | 351 | 351 | 9.51 | 1.15 | 10.66 | 0 | 0
67 | DGB-3 High Sea Gas (Dhuvaran) | Gas | State Gen | 376 | 376 | 9.53 | 1.11 | 10.64 | 0 | 0
68 | UGBPS-2 High Sea Gas | Gas | State Gen | 375 | 375 | 9.53 | 0.98 | 10.51 | 0 | 0
69 | GPPC High Sea Gas | Gas | State Gen | 703 | 703 | 9.64 | 0.77 | 10.41 | 0 | 0
70 | KAWAS Comm RLNG | Gas | State Gen | 182 | 656 | 9.82 | 0.84 | 10.66 | 4314 | 0
71 | GANDHAR RLNG | Gas | Central ISGS | 231 | 657 | 10.04 | 1.06 | 11.1 | 0 | 0
72 | KAWAS RLNG | Gas | Central ISGS | 182 | 656 | 10.1 | 0.84 | 10.94 | 0 | 0
73 | DGB-2 High Sea Gas | Gas | State Gen | 112 | 112 | 11 | 0.72 | 11.72 | 0 | 0
74 | DHUVARAN CCPP-III GSPC Spot | Gas | State Gen | 376 | 376 | 12.61 | 1.11 | 13.72 | 0 | 0
75 | UGBPS-2 GSPC Spot | Gas | State Gen | 375 | 375 | 12.61 | 0.98 | 13.59 | 0 | 0
76 | GSEG-2 Spot | Gas | State Gen | 351 | 351 | 12.63 | 1.15 | 13.78 | 0 | 0
77 | GPPC GSPC Spot | Gas | State Gen | 703 | 703 | 12.95 | 0.77 | 13.72 | 0 | 0
78 | DHUVARAN CCPP-II GSPC Spot | Gas | State Gen | 112 | 112 | 14.57 | 0.72 | 15.29 | 0 | 0
79 | KAWAS LIQUID | Gas | Central ISGS | 182 | 656 | 23.8 | 0.84 | 24.64 | 0 | 0 | Liquid fuel
TOTAL | [8 empty] | 528727 | 429312

## 5_COAL_SUPPLY_CURVE
INDIA COAL POWER SUPPLY CURVE 2024-25 ¦ Source: ICED CSV ¦ Gujarat plants highlighted
# | Plant Name | State | Capacity (MW) | Cumulative Cap (GW) | Total Cost (Rs/kWh) | Gujarat? | Note
1 | Chakabura power station | Chhattisgarh | 60 | 0.06 | 1.475
2 | Kasaipalli power station | Chhattisgarh | 270 | 0.33 | 1.475
3 | SWASTIK KORBA | Chhattisgarh | 25 | 0.355 | 1.475
4 | SASAN UMPP | Madhya Pradesh | 3960 | 4.315 | 1.504
5 | IND BARATH TPP | Odisha | 700 | 5.015 | 1.995
6 | Jaypee Nigrie Super Thermal Power Project | Madhya Pradesh | 1320 | 6.335 | 2.244
7 | Ennore Thermal Power Station | Tamil Nadu | 450 | 6.785 | 2.38
8 | BUDGE BUDGE | West Bengal | 750 | 7.535 | 2.393
9 | Singrauli Super Thermal Power Station | Uttar Pradesh | 2000 | 9.535 | 2.4
10 | BARSINGAR LIGNITE | Rajasthan | 250 | 9.785 | 2.589
11 | KORBA STPS | Chhattisgarh | 2600 | 12.385 | 2.608
12 | Talcher Kaniha Super Thermal Power Station | Odisha | 3000 | 15.385 | 2.762
13 | STERLITE TPP | Odisha | 600 | 15.985 | 2.78
14 | North Karanpura power station | Jharkhand | 1980 | 17.965 | 2.862
15 | Darlipali power station | Odisha | 1600 | 19.565 | 2.871
16 | Binjkote power station | Chhattisgarh | 600 | 20.165 | 2.88
17 | MP Amarkantak power station | Madhya Pradesh | 510 | 20.675 | 2.895
18 | Akrimota Power Project | Gujarat | 250 | 20.925 | 2.909 | ✅ YES | Gujarat plant – highlighted
19 | Sanjay Gandhi power station | Madhya Pradesh | 1340 | 22.265 | 2.964
20 | Rihand power station | Uttar Pradesh | 3000 | 25.265 | 3.011
21 | Kamalanga power station | Odisha | 1050 | 26.315 | 3.048
22 | SIPAT STPS | Chhattisgarh | 2980 | 29.295 | 3.199
23 | Southern Generating Power Station (Southern Repl. TPS) | West Bengal | 135 | 29.43 | 3.267
24 | Bakreshwar TPS | West Bengal | 1050 | 30.48 | 3.352
25 | Raigarh TRN Power Project | Chhattisgarh | 600 | 31.08 | 3.371
26 | Vindhyachal power station | Madhya Pradesh | 4760 | 35.84 | 3.406
27 | Sagardighi Thermal Power Station | West Bengal | 2260 | 38.1 | 3.439
28 | Ib Valley Thermal Power Station | Odisha | 1740 | 39.84 | 3.443
29 | Bela TPS | Maharashtra | 270 | 40.11 | 3.51
30 | Anpara-C power station | Uttar Pradesh | 1200 | 41.31 | 3.606
31 | Bandel Thermal Power Station | West Bengal | 450 | 41.76 | 3.611
32 | AMARAVATI TPP | Maharashtra | 1350 | 43.11 | 3.66
33 | Raigarh Project (Jindal) | Chhattisgarh | 1000 | 44.11 | 3.737
34 | Tenughat power station | Jharkhand | 420 | 44.53 | 3.842
35 | Dr. Shyama Prasad Mukherjee Thermal Power Station | Chhattisgarh | 500 | 45.03 | 3.87
36 | Hasdeo Thermal Power Station | Chhattisgarh | 1340 | 46.37 | 3.87
37 | Marwa power station | Chhattisgarh | 1000 | 47.37 | 3.87
38 | Anpara power station | Uttar Pradesh | 2630 | 50 | 3.877
39 | Guru Hargobind Lehra Mohabbat Power Station | Punjab | 920 | 50.92 | 3.89
40 | BALCO Korba power station | Chhattisgarh | 600 | 51.52 | 3.897
41 | Bara Thermal Power Project | Uttar Pradesh | 1980 | 53.5 | 3.912
42 | Lara STPS | Chhattisgarh | 1600 | 55.1 | 3.935
43 | BANDAKHAR TPP | Chhattisgarh | 300 | 55.4 | 3.937
44 | Mahadev Prasad Super Thermal Power Plant | Jharkhand | 540 | 55.94 | 3.938
45 | Obra TPS | Uttar Pradesh | 2852 | 58.792 | 3.984
46 | Kahalgaon Super Thermal Power Plant | Bihar | 2340 | 61.132 | 4.052
47 | GMR WARORA TPP | Maharashtra | 600 | 61.732 | 4.06
48 | Satpura Thermal Power Station | Madhya Pradesh | 1642.5 | 63.374 | 4.155
49 | Muthukur Mandal power station (Painampuram) | Andhra Pradesh | 1320 | 64.695 | 4.196
50 | Wardha Warora Power Plant | Maharashtra | 540 | 65.234 | 4.214
51 | Neyveli Thermal Power Station I | Tamil Nadu | 1470 | 66.704 | 4.215
52 | Tamnar power station | Chhattisgarh | 2400 | 69.105 | 4.228
53 | Maithon Right Bank Thermal Power Station | Jharkhand | 1050 | 70.154 | 4.229
54 | BHILAI TPP | Chhattisgarh | 500 | 70.654 | 4.255
55 | Baradarha power station | Chhattisgarh | 1200 | 71.855 | 4.259
56 | Ropar power station | Punjab | 1260 | 73.115 | 4.27
57 | Surat (Lignite) TPS | Gujarat | 500 | 73.615 | 4.27 | ✅ YES | Gujarat plant – highlighted
58 | Kolaghat Thermal Power Station | West Bengal | 1260 | 74.874 | 4.287
59 | Chhabra Thermal Power Station | Rajasthan | 2320 | 77.195 | 4.307
60 | AVANTHA BHANDAR TPP | Chhattisgarh | 600 | 77.794 | 4.309
61 | Uchpinda power station | Chhattisgarh | 1440 | 79.234 | 4.33
62 | HALDIA | West Bengal | 600 | 79.835 | 4.341
63 | Santaldih Thermal Power Station | West Bengal | 980 | 80.814 | 4.349
64 | PATHADI TPS PH -I | Chhattisgarh | 600 | 81.415 | 4.358
65 | Kota TPS | Rajasthan | 1240 | 82.654 | 4.479
66 | NTPC Seoni power station | Madhya Pradesh | 600 | 83.254 | 4.48
67 | Jawaharpur Thermal Project | Uttar Pradesh | 1320 | 84.575 | 4.49
68 | Durgapur DVC power station | West Bengal | 940 | 85.514 | 4.516
69 | Panki Thermal Power Station | Uttar Pradesh | 902 | 86.416 | 4.531
70 | Barauni power station | Bihar | 600 | 87.016 | 4.673
71 | Kalisindh Thermal Power Station | Rajasthan | 1200 | 88.216 | 4.688
72 | Rajpura Thermal Power Project | Punjab | 1400 | 89.617 | 4.688
73 | Shri Singaji MALWA TPP | Madhya Pradesh | 2520 | 92.136 | 4.691
74 | JALLIPPA KAPURDI TPP | Rajasthan | 1080 | 93.216 | 4.708
75 | Vizag Thermal Power Plant | Andhra Pradesh | 1040 | 94.257 | 4.73
76 | Dhariwal power station | Maharashtra | 600 | 94.856 | 4.738
77 | Khaparkheda TPS | Maharashtra | 1340 | 96.197 | 4.81
78 | Ramagundam power station | Telangana | 2600 | 98.796 | 4.877
79 | Kakatiya Thermal Power Project | Telangana | 1100 | 99.897 | 4.888
80 | DAMODARAM SANJEEVAIAH | Andhra Pradesh | 2400 | 102.296 | 4.9
81 | Anuppur power station (Newzone) | Madhya Pradesh | 1250 | 103.546 | 4.944
82 | Mundra Thermal Power Project (Adani) | Gujarat | 4620 | 108.166 | 4.965 | ✅ YES | Gujarat plant – highlighted
83 | Salaya power plant | Gujarat | 1200 | 109.367 | 4.976 | ✅ YES | Gujarat plant – highlighted
84 | Kodarma TPP | Jharkhand | 1000 | 110.367 | 4.988
85 | Talwandi Sabo Power Project | Punjab | 1980 | 112.347 | 4.989
86 | Ukai TPS | Gujarat | 1350 | 113.697 | 4.999 | ✅ YES | Gujarat plant – highlighted
87 | Muzaffarpur power station | Bihar | 610 | 114.306 | 5.001
88 | Kawai Thermal Power Project | Rajasthan | 1320 | 115.626 | 5.003
89 | Koradi Thermal Power Station | Maharashtra | 3020 | 118.647 | 5.03
90 | Mejia power station | West Bengal | 2340 | 120.987 | 5.048
91 | DURGAPUR STEEL TPS | West Bengal | 1000 | 121.987 | 5.075
92 | Tanda power station | Uttar Pradesh | 1760 | 123.746 | 5.099
93 | JSW RATNAGIRI TPP | Maharashtra | 300 | 124.046 | 5.11
94 | Yamuna Nagar or Deenbandhu Chotu Ram TPS | Haryana | 600 | 124.647 | 5.159
95 | Sabarmati power station | Gujarat | 362 | 125.008 | 5.173 | ✅ YES | Gujarat plant – highlighted
96 | Yadadri power station | Telangana | 2400 | 127.409 | 5.191
97 | Chandrapura power station | Jharkhand | 890 | 128.298 | 5.193
98 | Simhadri power station | Andhra Pradesh | 2000 | 130.298 | 5.22
99 | Goindwal Sahib Thermal Power Plant | Punjab | 540 | 130.839 | 5.266
100 | Khurja power station | Uttar Pradesh | 1320 | 132.159 | 5.273
101 | Ghatampur power station | Uttar Pradesh | 1320 | 133.478 | 5.282
102 | Mahatma Gandhi power station | Haryana | 1320 | 134.798 | 5.308
103 | Suratgarh Super Thermal Power Station | Rajasthan | 2820 | 137.619 | 5.343
104 | Bokaro Thermal Power Station | Jharkhand | 500 | 138.119 | 5.35
105 | MEJA STPP | Uttar Pradesh | 1320 | 139.439 | 5.358
106 | Hiranmaye Haldia power station | West Bengal | 300 | 139.738 | 5.366
107 | SINGARENI TPP | Telangana | 1200 | 140.939 | 5.392
108 | FARAKKA STPS | West Bengal | 2100 | 143.038 | 5.447
109 | Raghunathpur Thermal Power Station | West Bengal | 1200 | 144.238 | 5.455
110 | Gandhi Nagar TPS | Gujarat | 870 | 145.108 | 5.457 | ✅ YES | Gujarat plant – highlighted
111 | Chandrapur Thermal Power Station | Maharashtra | 3340 | 148.448 | 5.5
112 | Rajiv Gandhi Thermal Power Project | Haryana | 1200 | 149.649 | 5.5
113 | Bina TPS | Madhya Pradesh | 500 | 150.149 | 5.512
114 | Bhadradri power station | Telangana | 1080 | 151.228 | 5.533
115 | Dahanu power station | Maharashtra | 500 | 151.728 | 5.622
116 | Bhusawal Thermal Power Station | Maharashtra | 2135 | 153.863 | 5.66
117 | Paras power station | Maharashtra | 562.5 | 154.426 | 5.7
118 | Panipat power station | Haryana | 1360 | 155.786 | 5.707
119 | Gadarwara power station (BLA) | Madhya Pradesh | 90 | 155.876 | 5.736
120 | Kothagudem Thermal Power Station | Telangana | 2520 | 158.396 | 5.76
121 | Feroze Gandhi Unchahar Power Station | Uttar Pradesh | 1550 | 159.946 | 5.779
122 | Bongaigaon power station | Assam | 750 | 160.696 | 5.794
123 | Wanakbori Thermal Power Station | Gujarat | 2270 | 162.966 | 5.797 | ✅ YES | Gujarat plant – highlighted
124 | Mauda power station | Maharashtra | 2320 | 165.286 | 5.803
125 | SEMBCORP GAYATRI | Andhra Pradesh | 1320 | 166.606 | 5.98
126 | Thoothukudi IBTPL power station | Tamil Nadu | 1050 | 167.656 | 6.066
127 | Nabinagar Thermal Power Project | Bihar | 1980 | 169.636 | 6.082
128 | Sri Damodaram Sanjeevaiah Thermal Power Station | Andhra Pradesh | 2400 | 172.036 | 6.1
129 | Dr. Narla Tata Rao Thermal power station | Andhra Pradesh | 2560 | 174.596 | 6.1
130 | North Chennai Thermal Power Station | Tamil Nadu | 2630 | 177.226 | 6.128
131 | Rayalaseema Thermal Power Project | Andhra Pradesh | 1650 | 178.876 | 6.15
132 | Vallur Thermal Power Plant | Tamil Nadu | 1500 | 180.376 | 6.181
133 | TIRORA TPP | Maharashtra | 3300 | 183.676 | 6.216
134 | Gadarwara Super Thermal Power Project | Madhya Pradesh | 1600 | 185.276 | 6.406
135 | Khargone power station | Madhya Pradesh | 1320 | 186.596 | 6.416
136 | INDRA GANDHI STPP | Haryana | 1500 | 188.096 | 6.654
137 | Solapur power station | Maharashtra | 1320 | 189.416 | 6.756
138 | Barh I power station | Bihar | 3300 | 192.716 | 6.82
139 | DADRI (NCTPP) | Uttar Pradesh | 1820 | 194.536 | 7.016
140 | Trombay power station | Maharashtra | 1400 | 195.936 | 7.234
141 | NASIK | Maharashtra | 880 | 196.816 | 7.24
142 | Ramagudem -B TPS | Telangana | 62.5 | 196.879 | 7.297
143 | Kudgi STPP | Karnataka | 2400 | 199.279 | 7.349
144 | Raichur Thermal Power Station | Karnataka | 1720 | 200.999 | 7.41
145 | Bellary Thermal Power Station | Karnataka | 1700 | 202.698 | 7.532
146 | Bhavnagar power station | Gujarat | 500 | 203.198 | 7.739 | ✅ YES | Gujarat plant – highlighted
147 | Kutchh Lignite TPS | Gujarat | 290 | 203.488 | 7.745 | ✅ YES | Gujarat plant – highlighted
148 | Rosa TPP | Uttar Pradesh | 1200 | 204.689 | 8.016
149 | Mettur Thermal Power Station | Tamil Nadu | 1440 | 206.129 | 8.095
150 | Yermarus power station | Karnataka | 1600 | 207.728 | 8.505
151 | Parli Thermal Power Station | Maharashtra | 1420 | 209.149 | 8.53
152 | Udupi power station | Karnataka | 1200 | 210.349 | 9.17
153 | Sikka Thermal Power Station | Gujarat | 740 | 211.089 | 10.705 | ✅ YES | Gujarat plant – highlighted

## 6_RAMP_RATES
⚠️ RAMP RATES – CEA/CERC REGULATORY PROXY ¦ No Gujarat-unit-specific data publicly available ¦ Source: CEA Standards + CERC Dec-2023
NOTE: These values are derived from CEA standards and CERC December 2023 flexibility regulations. Unit-specific ramp rates for Gujarat plants must be obtained from GSECL/IPP technical data or commissioning reports. Update this sheet when actual data is available.
# | Generator / Station | Unit Size (MW) | Technology | Fuel | Ramp Rate Up (MW/min) | Ramp Rate Down (MW/min) | Basis / Regulatory Source | Min Load Band | Must Verify
1 | GANDHINAGAR TPS Gr 3-5 | 210 | Sub-critical | Coal | 2.1 | 2.1 | CEA std 1%/min (sub-critical, 40-55% load) | 40-55% MCR | YES – get from GSECL
2 | WANAKBORI TPS | 210 | Sub-critical | Coal | 2.1 | 2.1 | CEA std 1%/min | 40-55% MCR | YES – get from GSECL
3 | UKAI TPS Gr 1-5 | 200 | Sub-critical | Coal | 2 | 2 | CEA std 1%/min | 40-55% MCR | YES – get from GSECL
4 | UKAI TPS Unit 6 | 500 | Super-critical | Coal | 10 | 10 | CEA std 2%/min (super-critical) | 40-55% MCR | YES – get from GSECL
5 | SIKKA TPS 3-4 | 250 | Sub-critical | Coal | 2.5 | 2.5 | CEA std 1%/min | 40-55% MCR | YES – get from GSECL
6 | AKRIMOTA (BECL) | 125 | Sub-critical | Lignite | 1.3 | 1.3 | CEA std 1%/min | 40-55% MCR | YES – get from BECL
7 | SLPP (GIPCL) | 125 | Sub-critical | Lignite | 1.3 | 1.3 | CEA std 1%/min | 40-55% MCR | YES – get from GIPCL
8 | ADANI MUNDRA Stage-1 | 330 | Super-critical | Coal | 6.6 | 6.6 | CEA std 2%/min | 40-55% MCR | YES – get from Adani
9 | ADANI MUNDRA Stage-2 | 660 | Super-critical | Coal | 19.8 | 19.8 | CEA std 3%/min (ultra-SC) | 40-55% MCR | YES – get from Adani
10 | EPGL (Essar) | 600 | Super-critical | Coal | 12 | 12 | CEA std 2%/min | 40-55% MCR | YES – get from Essar
11 | CGPL MUNDRA UMPP | 830 | Super-critical | Coal | 24.9 | 24.9 | CEA std 3%/min | 40-55% MCR | YES – get from Tata Power
12 | SUGEN / UNOSUGEN CCPP | 1148 | CCGT | Gas | 57.4 | 57.4 | CCGT 5%/min (IEA benchmark) | 30% MCR | YES – get from Torrent
13 | DHUVARAN CCPP | 595 | CCGT | Gas | 29.8 | 29.8 | CCGT 5%/min | 30% MCR | YES – get from GSECL
14 | UTRAN-II CCPP | 375 | CCGT | Gas | 18.8 | 18.8 | CCGT 5%/min | 30% MCR | YES – get from GSECL
15 | JHANOR-JGPS / KAWAS | 657 | OCGT | Gas | 52.6 | 52.6 | OCGT 8%/min (fast start) | 15% MCR | YES – get from NTPC
16 | UKAI HYDRO | 305 | Hydro | Hydro | 45.8 | 45.8 | Hydro ~15%/min (IEA) | 0-10% MCR | YES – get from GSECL
17 | KADANA HYDRO | 242 | Hydro | Hydro | 36.3 | 36.3 | Hydro ~15%/min | 0-10% MCR | YES – get from GSECL
18 | SSP (Sardar Sarovar) | 1450 | Hydro | Hydro | 217.5 | 217.5 | Hydro ~15%/min | 0-10% MCR | YES – get from SSNNL

## 7_MISSING_DATA
❌ MISSING DATA TRACKER – REQUIRED FOR GAMS SCED/SCUC MODEL
# | Data Parameter | Why Needed in GAMS Model | Granularity Required | Source to Approach | Priority | Status
1 | Transmission Network Model (Bus topology, line impedance R/X, thermal limits – 220kV/400kV) | Core of 'SC' in SCED/SCUC – DC Power Flow / PTDF matrix; without this only zonal model possible | Line-level: impedance, Smax (MVA), from-bus / to-bus | GETCO Network Planning Dept | P1 – CRITICAL | ❌ Not Available
2 | Bus-wise / Zonal Load Data (96 time-blocks × zone per day) | Nodal or zonal demand constraint in SCED; needed every 15-min block | 15-min blocks × N zones; day-ahead and actual | SLDC / DISCOMs (DGVCL, MGVCL, UGVCL, PGVCL) | P1 – CRITICAL | ❌ Not Available
3 | RE Generation Forecast Profile (Wind & Solar – 15-min block) | Must-run RE injection → residual demand → curtailment optimization objective | 15-min MW forecast per RE zone / aggregated | SLDC REMC / GUVNL RE forecast team | P1 – CRITICAL | ❌ Not Available
4 | Central Sector Drawal Schedule (ISGS unit-wise 96-block schedule from WRLDC) | ISGS units are must-take/partially firm; constrains state dispatch headroom | 15-min block × ISGS unit; daily schedule | WRLDC / POSOCO drawal schedule portal | P1 – CRITICAL | ❌ Not Available
5 | Minimum Up Time / Down Time (MUT/MDT per thermal unit) | Binary UC constraint – unit cannot start/stop faster than MUT/MDT | Hours per unit | GSECL / IPP commissioning reports; CERC petitions | P2 – HIGH | ⚠️ Use generic proxy
6 | Startup & Shutdown Costs (Cold/warm/hot start cost per unit) | UC objective function includes startup cost to avoid unnecessary cycling | Rs per startup event (cold/warm/hot); per unit | GERC tariff petitions (GSECL, GIPCL, Adani etc.) | P2 – HIGH | ⚠️ Derive from tariff orders
7 | No-Load (Fixed O&M) Cost (per hour per committed unit) | Two-part cost in UC – generator incurs cost even at Pmin | Rs/hr per unit | GERC / CERC tariff orders | P2 – HIGH | ⚠️ Partially in Sheet 4
8 | Unit-Specific Ramp Rates (Actual measured, not CEA proxy) | UC/ED ramp constraint – limits inter-period generation change | MW/min up and down per unit | GSECL / IPP O&M dept; CEA performance reports | P2 – HIGH | ⚠️ Proxy in Sheet 6
9 | Spinning Reserve Requirement (State & inter-state obligation) | UC must ensure adequate online reserve ≥ state policy / IEGC obligation | MW per time-block; percentage of peak | SLDC operational policy; IEGC / GERC Grid Code 2026 | P2 – HIGH | ❌ Not Available
10 | Hydro Reservoir & Water Availability (SSP, Kadana, Ukai Hy – daily/seasonal) | Hydro dispatch is water-energy constrained; water availability limits generation | MWh / m³ daily; seasonal profile | SSNNL / GSECL Hydro; CWC reservoir bulletins | P2 – HIGH | ❌ Not Available
11 | Gas Fuel Nomination & Tier Availability (APM / Non-APM / RLNG / Spot per day) | Same gas plant has 4 different cost tiers; daily nomination determines which tier is active | MMSCMD per tier per gas station per day | GAIL daily nominations; GSPC gas supply contracts | P2 – HIGH | ❌ Not Available
12 | Planned / Forced Outage Schedule (Unit availability flag per time-block) | UC must skip unavailable units; outage schedule = availability parameter | Binary (0/1) per unit per time-block | SLDC / GSECL outage coordination; POSOCO NOAR | P2 – HIGH | ❌ Not Available
13 | Historical RE Curtailment Data | Model validation – compare GAMS output vs. actual curtailment events | MWh curtailed per RE zone per day | SLDC internal logs; GUVNL RE scheduling | P3 – MEDIUM | ❌ Not Available
14 | ATC / Inter-Regional Transfer Limits (Gujarat ↔ WR corridor limits) | Boundary constraint on import/export from/to WR grid | MW per time-block (seasonal ATC) | WRLDC; GUVNL LTOA/MTOA corridor data | P3 – MEDIUM | ⚠️ Rough estimate possible
15 | Heat Rate Curves (input-output or incremental heat rate per unit) | For a cost-accurate SCED, piecewise linear heat rate is more accurate than flat variable cost | Piecewise linear: MW blocks vs. kcal/kWh | CEA Annual Performance Reports; POSOCO SCED dataset | P3 – MEDIUM | ⚠️ ICED CSV gives proxy
✅ UPDATES FROM WRLDC PSP REPORT (30-May-2026): #4 ISGS Drawal → RESOLVED (Sheet 9) ¦ #10 Hydro Reservoir → RESOLVED (Sheet 11) ¦ #13 RE Curtailment → RESOLVED (Sheet 10: Solar 2.21 MU + Wind 0.69 MU curtailed on 30-May-2026) ¦ #14 ATC/IR Limits → PARTIALLY RESOLVED (Sheet 12)
⚠️ UPDATE (GETCO Power Map 01-Sep-2023): #11 Transmission Network → PARTIALLY RESOLVED — Bus topology + line connectivity in Sheets 13–15. R/X impedances + MVA thermal limits still UNKNOWN. Full nodal model still requires GETCO data.
✅ UPDATES FROM EXTERNAL SEARCH (Jun-2026): #7 MUT/MDT → NOW IN Sheet 16 (CEA proxy) ¦ #8 Startup costs → Partially in Sheet 16 (cold/warm/hot time proxies) ¦ #9 Spinning Reserve → Framework in Sheet 19 (GERC BESS 2026 + IEGC) ¦ #12 Outage rates → Framework + FOR% in Sheet 18 (CEA norms) ¦ #15 Heat rates → Normative values in Sheet 16 (CEA 2024-29 norms) ¦ Still MISSING: Line impedances, 96-block load data, RE forecast, gas nominations
✅ REPRODUCED DATA ADDED (Jun-2026 — All remaining gaps filled by engineering estimates): Sheet 21: 96-block load (🔴REPR, 3 AUTH anchors) ¦ Sheet 22: RE generation profile (🔴REPR, 2 AUTH anchors) ¦ Sheet 23: Line impedances R/X/B (🟠PROXY — standard ACSR) ¦ Sheet 24: Startup/no-load costs + MUT/MDT (🟠PROXY+🔴REPR) ¦ Sheet 25: Gas nomination tiers (🟢AUTH prices + 🔴REPR volumes) ¦ ⚠️ NO CRITICAL DATA GAPS REMAIN — All parameters available for GAMS model build. Reproduced data MUST be validated with SLDC/GETCO/GSECL before production use.

## 8_GUJ_ACTUAL_GEN
GUJARAT ACTUAL GENERATION ¦ Source: WRLDC PSP Report ¦ Date: 30-May-2026
# | Station | Fuel | Inst Cap (MW) | Peak MW (20:00) | Off-Peak MW (03:00) | Day Peak (MW) | Peak Time | Min Gen 06-18h (MW) | Gross Energy (MU) | Net Energy (MU) | Avg (MW)
1 | AECO / TP-AECO | Thermal | 362 | 348 | 358 | 362 | 03:25 | 225 | 7.4 | 6.73 | 280
2 | AKRIMOTA (ALTPS) | Thermal | 250 | 102 | 120 | 162 | 00:03 | 105 | 3.13 | 2.67 | 111
3 | APL MUNDRA (Adani) | Thermal | 4620 | 3391 | 2996 | 4019 | 23:49 | 2391 | 77.35 | 70.84 | 2952
4 | BLTPS (BECL) | Thermal | 500 | 304 | 247 | 316 | 21:25 | 236 | 6.89 | 5.73 | 239
5 | GANDHINAGAR TPS (GTPS) | Thermal | 630 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
6 | KLTPS | Thermal | 150 | 64 | 59 | 65 | 00:16 | 57 | 1.51 | 1.33 | 55
7 | OTHER CPP | Thermal | 1000 | 0 | 0 | 0 | — | 0 | 7.2 | 5.94 | 248
8 | SLPP (GIPCL) | Thermal | 500 | 380 | 336 | 404 | 00:32 | 258 | 9.41 | 8.15 | 340
9 | STPS (Sikka) | Thermal | 500 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
10 | UKAI TPS | Thermal | 1110 | 680 | 496 | 687 | 23:57 | 387 | 13.39 | 12.36 | 515
11 | VADINAR (EPGL / Essar) | Thermal | 1200 | 723 | 621 | 1132 | 09:30 | 606 | 19.09 | 17.86 | 744
12 | WANAKBORI TPS | Thermal | 2270 | 1094 | 910 | 1133 | 00:00 | 680 | 22.01 | 20.37 | 849
13 | DGBPS (Dhuvaran CCPP) | Gas | 594 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
14 | ESSAR POWER GAS | Gas | 515 | 0 | 0 | 0 | — | 0 | 0 | 0 | 0
15 | GIPCL STG-1 | Gas | 145 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
16 | GIPCL STG-2 | Gas | 165 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
17 | GPEC (GSPC Pipavav CLPI) | Gas | 654 | 0 | 0 | 0 | — | 0 | 0 | 0 | 0
18 | GPPC | Gas | 702 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
19 | GSEG (GSEC) | Gas | 156 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
20 | SUGEN CCPP (Torrent) | Gas | 1148 | 648 | 181 | 649 | 19:02 | -2 | 5.69 | 5.46 | 228
21 | UNOSUGEN (Torrent) | Gas | 383 | -1 | -2 | 274 | 00:00 | -2 | 0.15 | 0.1 | 4
22 | UTRAN STG-II | Gas | 375 | 0 | 0 | 0 | 00:00 | 0 | 0 | 0 | 0
23 | KADANA HYDRO | Hydro | 240 | 53 | 50 | 54 | 18:53 | 0 | 0.54 | 0.54 | 23
24 | LBC PANAM HYDRO | Hydro | 5 | 0 | 0 | 0 | — | 0 | 0.08 | 0.08 | 3
25 | PVT HYDRO (Small) | Hydro | 20.6 | 0 | 0 | 0 | — | 0 | 0.15 | 0.15 | 6
26 | UKAI HYDRO | Hydro | 300 | 69 | 70 | 71 | 01:32 | 69 | 1.71 | 1.67 | 70
27 | WIND (8,836 MW installed) | Wind | 8836 | 6092 | 5914 | 6153 | 20:06 | 3376 | 124.34 | 124.34 | 5181
28 | SOLAR (15,238 MW inst.) | Solar | 15238 | 0 | 0 | 9993 | 12:08 | 0 | 75.73 | 75.73 | 3155
29 | BIOMASS | Biomass | 51.65 | 0 | 0 | 0 | — | 0 | 0 | 0 | 0
TOTAL GUJARAT | [8 empty] | 375.77 | 360.05
GUJARAT SUMMARY (30-May-2026): Evening Peak Demand: 22,145 MW ¦ Off-Peak: 20,185 MW ¦ Max Demand: 26,093 MW @ 15:30 ¦ Day Consumption: 534.5 MU ¦ Zero shortage

## 9_ISGS_DRAWAL
ISGS ACTUAL GENERATION & GUJARAT ALLOCATED SHARE ¦ Source: WRLDC PSP 30-May-2026
# | ISGS Station | Fuel | Inst Cap (MW) | Guj Share (MW) | Peak MW (20:00) | Off-Peak MW (03:00) | Day Peak (MW) | Min Gen (MW) | Scheduled (MU) | Gross (MU) | Net (MU) | Avg (MW)
1 | GADARWARA (2×800) | Coal | 1600 | 333.83 | 1131 | 800 | 1476 | 740 | 20.97 | 22.8 | 21.05 | 877
2 | GANDHAR GAS | Gas | 657 | 237 | 0 | -13 | 14 | -25 | 0.03 | 0.05 | 0.05 | 2
3 | KAPS 1&2 (Kakrapar) | Nuclear | 440 | 125 | 391 | 391 | 391 | 391 | 9.55 | 10.49 | 9.48 | 395
4 | KAPS 3&4 (Kakrapar Ext) | Nuclear | 1400 | 475.88 | 591 | 599 | 603 | 589 | 28.86 | 31.49 | 28.91 | 1205
5 | KAWAS GAS | Gas | 656 | 187 | -7 | -3 | 37 | -23 | 0.02 | 0 | 0 | 0
6 | KHARGONE STPS | Coal | 1320 | 270.2 | 791 | 660 | 1039 | 662 | 16.63 | 18.75 | 17.23 | 718
7 | KORBA KSTPS 1&2 | Coal | 2100 | 380.84 | 1324 | 1300 | 1379 | 744 | 30.48 | 32.81 | 30.19 | 1258
8 | KORBA KSTPS-3 | Coal | 500 | 130.34 | 473 | 466 | 490 | 278 | 9.67 | 10.37 | 9.65 | 402
9 | LARA STPS (2×800) | Coal | 1600 | 186.48 | 709 | 732 | 745 | 392 | 15.19 | 16.79 | 14.98 | 624
10 | MAUDA-I (MOUDA) | Coal | 1000 | 455.63 | 778 | 680 | 840 | 427 | 14.85 | 16.31 | 14.59 | 608
11 | MAUDA-II (MOUDA) | Coal | 1320 | 530.24 | 1048 | 915 | 1130 | 575 | 18.82 | 21.22 | 18.54 | 773
12 | NSPCL (JV) | Coal | 500 | See Sh.1 | 428 | 422 | 478 | 234 | 8.79 | 9.76 | 8.88 | 370
13 | RGPPL (Gas JV) | Gas | 1967 | See Sh.1 | -18 | -8 | 17 | -35 | 0.12 | 0.12 | 0.12 | 5
14 | SASAN UMPP (Reliance) | Coal | 3960 | See Sh.1 | 3744 | 3751 | 3776 | 1969 | 78.02 | 84.6 | 79.26 | 3303
15 | SIPAT-I (3×660) | Coal | 1980 | 576.99 | 1863 | 1840 | 1938 | 973 | 37.88 | 40.73 | 38.26 | 1594
16 | SIPAT-II (2×500) | Coal | 1000 | 286.02 | 933 | 916 | 969 | 485 | 19.33 | 20.63 | 19.37 | 807
17 | SOLAPUR STPS (2×660) | Coal | 1320 | See Sh.1 | 659 | 660 | 822 | 661 | 16.26 | 18.7 | 17.23 | 718
18 | SSP RBPH+CHPH | Hydro | 1450 | 232 | 492 | 437 | 1081 | 47 | 6.74 | 7.57 | 7.47 | 311
19 | TARAPUR 1&2 (TAPS) | Nuclear | 320 | 160 | 152 | 152 | 155 | 103 | 3.5 | 3.84 | 3.4 | 142
20 | TARAPUR 3&4 (TAPS) | Nuclear | 1080 | 274 | 793 | 791 | 847 | 763 | 18.6 | 20.98 | 18.71 | 780
21 | VSTPS-I (6×210) | Coal | 1260 | 247.74 | 873 | 922 | 933 | 508 | 18.6 | 20.62 | 18.07 | 753
22 | VSTPS-II (2×500) | Coal | 1000 | 252.64 | 896 | 904 | 932 | 514 | 18.41 | 19.56 | 18.06 | 753
23 | VSTPS-III (2×500) | Coal | 1000 | 279.64 | 886 | 877 | 962 | 518 | 18.44 | 19.39 | 18.38 | 766
24 | VSTPS-IV (2×500) | Coal | 1000 | 258.6 | 889 | 881 | 960 | 485 | 18.63 | 20.08 | 18.65 | 777
25 | VSTPS-V (1×500) | Coal | 500 | 102.79 | 434 | 434 | 488 | 243 | 9.2 | 9.86 | 9.27 | 386

## 10_GUJ_DEMAND_CURT
GUJARAT DEMAND, GENERATION MIX & RE CURTAILMENT ¦ Source: WRLDC PSP 30-May-2026
A. DEMAND PROFILE – GUJARAT
Parameter | Evening Peak (20:00) | Off-Peak (03:00) | Max Demand (MW) | Time of Max | Day Avg (MW) | Day Consumption (MU) | Forecast (MU)
Demand Met | 22145 | 20185 | 26093 | 15:30 | 22272 | 534.5 | 529
Shortage (MW) | 0 | 0 | 0 | — | 0 | 0 | 0
ACE Max / Min | 2061.41 | -974.96 | — | 12:37/07:31 | — | — | —
Frequency (Hz) | 50.08 | 50.03 | — | — | — | — | —
B. GENERATION MIX – GUJARAT (State Control Area Only)
Fuel Type | Net Energy (MU) | % Share | Avg MW | Peak MW (20:00) | Off-Peak MW (03:00) | Notes
Thermal (Coal/Lignite) | 151.98 | 42.21% | 6333 | 7086 | 6143 | Incl GSECL + Adani + Essar + GIPCL
Gas | 5.56 | 1.544% | 232 | 647 | 179 | Only Sugen+Unosugen active; all others at 0
Hydro | 2.44 | 0.6777% | 102 | 122 | 120 | Kadana + Ukai Hy + Small
Wind | 124.34 | 34.53% | 5181 | 6092 | 5914 | 8,836 MW installed; CF ~59% on this day
Solar | 75.73 | 21.03% | 3155 | 0 | 0 | 15,238 MW inst; peaks 9,993 MW at 12:08
Biomass | 0 | 0% | 0 | 0 | 0 | Not dispatched on this day
TOTAL | 360.05 | 100.0%
C. RE CURTAILMENT – GUJARAT (30-May-2026) ⚠️ KEY MODEL VALIDATION DATA
Type | Max MW Curtailed | Energy Curtailed (MU) | Reason | Significance
Wind Curtailment | 554 | 0.69 | To control Under-Drawal (UD) | Wind curtailed → RE curtailment is REAL in Gujarat grid
Solar Curtailment | 1684 | 2.21 | To control Under-Drawal (UD) | 1,684 MW solar curtailed at midday — core model objective to minimize this
TOTAL RE Curtailed | — | 2.9 | UD Management | 2.90 MU on single day — annualise to estimate curtailment problem scale

## 11_RESERVOIR_LEVELS
MAJOR RESERVOIR LEVELS ¦ Source: WRLDC PSP 30-May-2026 ¦ Gujarat reservoirs highlighted
Reservoir | MDDL (m) | FRL (m) | Design Energy (MU) | Present Level (m) | Present Energy (MU) | Last Year Level (m) | Last Year Energy (MU) | Remarks
SSP (Sardar Sarovar) ✅ | 110.64 | 138.68 | 1342.091 | 128.55 | 632.95 | 122.47 | 344.14 | Gujarat ¦ Present >> Last Year → more hydro energy available
UKAI (Reservoir) ✅ | 82.296 | 105.156 | 770.67 | 96.4 | 298.58 | 96.937 | 320.919 | Gujarat ¦ Present ≈ Last Year
KADANA (Reservoir) ✅ | 114.3 | 127.711 | 126.266 | 121.18 | 37.59 | 117.928 | 14.57 | Gujarat ¦ Present > Last Year → more energy available
INDIRASAGAR (MP) | 243.23 | 262.13 | 1367 | 250.19 | 314.88 | 252.31 | 413.61 | MP – for WR context
OMKARESHWAR (MP) | 193.3 | 196.6 | 21.958 | 194.4 | — | 196.23 | — | MP – for WR context
KOYNA (Maharashtra) | 615.54 | 659.43 | 3160 | 623.1 | 18.655 | 628.7 | 11.985 | Maharashtra – for WR context
TATA BHIRA (Mah) | 590.1 | 607.1 | 582.4 | 594.7 | 124.86 | 594.99 | 134.9 | Maharashtra – for WR context

## 12_IR_EXCHANGE
WR INTER-REGIONAL EXCHANGE & GUJARAT SCHEDULE ¦ Source: WRLDC PSP 30-May-2026
A. STATE-WISE DAY ENERGY SCHEDULE (Section 4B) — Gujarat row in green
State | ISGS+GNA Schedule (MU) | T-GNA Bilateral (MU) | GDAM (MU) | DAM (MU) | RTM (MU) | Total Schedule (MU) | Note
AMNSIL | 8.38 | 0 | 0.52 | 1.07 | 2.69 | 12.66
BALCO | 17.12 | 0 | 0 | 0 | 0 | 17.12
CHHATTISGARH | 79.01 | -0.45 | -0.01 | -2.7 | -4.83 | 71.02 | Net exporter
DNHDDPDCL | 23.54 | 1.59 | 0 | 4.18 | 1.36 | 30.68
GOA | 16.02 | 3.52 | 0 | -1.13 | -0.62 | 17.8
GUJARAT ✅ | 143.87 | 12.68 | 3.6 | 6.95 | 7.38 | 174.49 | Total drawal from all market segments
MADHYA PRADESH | 143.79 | -1.58 | 1 | 8.38 | 8.21 | 159.8
MAHARASHTRA | 193.75 | 3.16 | 1.53 | 18.83 | 50.33 | 267.58
RIL JAMNAGAR | 6.38 | 0 | 0.23 | 0 | 0 | 6.61
TOTAL (WR) | 631.86 | 18.92 | 6.87 | 35.58 | 64.52 | 757.76
B. WR TOTAL NET INTER-REGIONAL EXPORT (30-May-2026): WR→ER: -17.21 MU ¦ WR→NR: -149.01 MU ¦ WR→SR: -87.40 MU ¦ TOTAL NET: -253.62 MU (WR is net exporter)
C. FREQUENCY PROFILE (WR 30-May-2026)
Parameter | Value
Maximum Frequency | 50.30 Hz | Time: 08:43
Minimum Frequency | 49.73 Hz | Time: 22:36
Average Frequency | 50.00 Hz | Within IEGC nominal
% Time outside IEGC Band | 23.8% | ⚠️ Significant — 5.71 hrs outside band
Freq Variation Index | 0.068 | Standard deviation
Max in 15-min block | 50.28 Hz
Min in 15-min block | 49.82 Hz

## 13_NETWORK_TOPOLOGY
GUJARAT TRANSMISSION NETWORK TOPOLOGY ¦ Source: GETCO Power Map 01-Sep-2023 ¦ ⚠️ Topology only — impedance/MVA limits require GETCO network data
NOTE: Bus names, voltage levels, zones and connectivity extracted visually from GETCO Power Map. R/X impedance values and thermal limits (MVA) are NOT available from this map and must be obtained from GETCO Network Planning. This sheet establishes the bus list and zonal topology for the GAMS model.
A. BUS / SUBSTATION LIST — Identified from GETCO Power Map (01-Sep-2023)
# | Substation / Bus Name | Voltage Level(s) | Zone / Region | District | Connected Generators | Bus Type (Gen/Load/Trans) | Coordinates (Approx) | Source | Remarks
1 | MUNDRA (Tata UMPP / Adani) | 400kV | Kutch | Kutch | APL Mundra, CGPL Mundra UMPP | Generator | 23.0N, 69.7E | Power Map | HVDC bipole terminal; major export bus
2 | BHIMASAR | 400kV, 220kV | Kutch | Kutch | — | Transmission | 23.1N, 69.8E | Power Map | Key 400kV switching hub in Kutch
3 | VADINAR (ESSAR) | 220kV | Kutch | Kutch | EPGL (Essar Power) | Generator | 22.5N, 69.8E | Power Map
4 | AKRIMOTA / PANANDHRO | 220kV | Kutch | Kutch | Akrimota Lignite TPS | Generator | 23.6N, 68.9E | Power Map | BECL plant
5 | KHAVDA-1 (PSTS) | 765kV, 400kV | Kutch | Kutch | Large RE solar park | Transmission | 23.8N, 69.6E | Power Map | New 765kV hub for RE evacuation
6 | KHAVDA-2 (PSTS) | 765kV | Kutch | Kutch | RE Solar Park | Transmission | 23.7N, 69.7E | Power Map | Proposed/new RE bus
7 | CHARANKA SOLAR PARK | 220kV | Kutch/Patan | Patan | Charanka Solar (GSECL) | Generator | 23.9N, 71.2E | Power Map | Large solar park
8 | VANSANA | 400kV | Kutch | Kutch | Wind farms | Transmission | 23.0N, 70.2E | Power Map
9 | BHUJ (PGCIL) | 400kV | Kutch | Kutch | — | Transmission | 23.3N, 69.7E | Power Map | Inter-regional bus
10 | DHOLERA | 220kV | Kutch | Ahmedabad | — | Transmission | 22.2N, 72.2E | Power Map
11 | SIKKA | 220kV | Saurashtra | Jamnagar | Sikka TPS (GSECL) | Generator | 22.4N, 69.9E | Power Map
12 | RAJKOT | 220kV | Saurashtra | Rajkot | — | Load/Trans | 22.3N, 70.8E | Power Map | Major load bus
13 | JETPUR | 400kV | Saurashtra | Rajkot | — | Transmission | 21.7N, 70.6E | Power Map | 400kV hub
14 | AMRELI | 220kV | Saurashtra | Amreli | — | Load/Trans | 21.6N, 71.2E | Power Map
15 | JUNAGADH | 220kV | Saurashtra | Junagadh | — | Load/Trans | 21.5N, 70.5E | Power Map
16 | PIPAVAV (GSPC) | 220kV | Saurashtra | Amreli | GSPC Pipavav CLPI | Generator | 20.9N, 71.5E | Power Map | Gas plant
17 | BHAVNAGAR | 220kV | Saurashtra | Bhavnagar | — | Load/Trans | 21.8N, 72.2E | Power Map
18 | JAMNAGAR | 220kV | Saurashtra | Jamnagar | — | Load/Trans | 22.5N, 70.1E | Power Map
19 | MORBI | 220kV | Saurashtra | Morbi | — | Load/Trans | 22.8N, 70.8E | Power Map
20 | WANKANER | 220kV | Saurashtra | Morbi | — | Transmission | 22.6N, 71.0E | Power Map
21 | HALVAD | 220kV | Saurashtra | Morbi | Wind farms | Transmission | 23.0N, 71.2E | Power Map | Wind evacuation
22 | KANSARI (NERDA) | 765kV, 400kV | North Gujarat | Banaskantha | — | Transmission | 24.1N, 72.4E | Power Map | 765kV WR–NR interchange point
23 | BANASKANTHA | 220kV | North Gujarat | Banaskantha | — | Load/Trans | 24.2N, 72.0E | Power Map
24 | MEHSANA | 220kV | North Gujarat | Mehsana | — | Load/Trans | 23.6N, 72.4E | Power Map
25 | PATAN | 220kV | North Gujarat | Patan | — | Load/Trans | 23.9N, 72.1E | Power Map
26 | SIDDHPUR | 220kV | North Gujarat | Patan | — | Transmission | 23.9N, 72.4E | Power Map
27 | SABARKANTHA | 220kV | North Gujarat | Sabarkantha | — | Load/Trans | 23.6N, 73.0E | Power Map
28 | MAHISAGAR / MODASA | 220kV | North Gujarat | Mahisagar | — | Load/Trans | 23.5N, 73.3E | Power Map
29 | GANDHINAGAR (GTPS) | 220kV | Central | Gandhinagar | Gandhinagar TPS (GSECL) | Generator | 23.2N, 72.7E | Power Map | State capital; major gen bus
30 | DEHGAM | 400kV, 220kV | Central | Gandhinagar | — | Transmission | 23.3N, 73.0E | Power Map | 400kV hub; connects to PGCIL
31 | RANASAN | 400kV | Central | Gandhinagar | — | Transmission | 23.4N, 72.6E | Power Map
32 | RANA (PGCIL) | 765kV | Central | Gandhinagar | — | Transmission | 23.2N, 72.6E | Power Map | Inter-regional 765kV hub
33 | WANAKBORI | 220kV | Central | Kheda | Wanakbori TPS (GSECL) | Generator | 22.9N, 73.2E | Power Map | 7+1 units; major coal gen
34 | KADANA | 220kV | Central | Mahisagar | Kadana Hydro | Generator | 23.3N, 73.7E | Power Map
35 | ANAND | 220kV | Central | Anand | — | Load/Trans | 22.6N, 72.9E | Power Map
36 | VADODARA (PGCIL) | 400kV | East Gujarat | Vadodara | — | Transmission | 22.3N, 73.2E | Power Map | SLDC located here; key hub
37 | KASOR | 400kV | East Gujarat | Vadodara | — | Transmission | 22.3N, 73.1E | Power Map
38 | PANCHMAHAL | 220kV | East Gujarat | Panchmahal | — | Load/Trans | 22.8N, 73.6E | Power Map
39 | GODHRA | 220kV | East Gujarat | Panchmahal | — | Load/Trans | 22.8N, 73.6E | Power Map
40 | UKAI | 220kV | South Gujarat | Tapi | Ukai TPS + Hydro (GSECL) | Generator | 21.3N, 73.6E | Power Map | Both thermal and hydro
41 | SURAT (PGCIL) | 400kV, 220kV | South Gujarat | Surat | — | Transmission | 21.2N, 72.8E | Power Map | Major 400kV hub
42 | NAVSARI | 220kV | South Gujarat | Navsari | — | Load/Trans | 20.9N, 73.0E | Power Map
43 | VALSAD | 220kV | South Gujarat | Valsad | — | Load/Trans | 20.6N, 73.0E | Power Map | To Maharashtra border
44 | HAZIRA | 400kV | South Gujarat | Surat | Essar/ONGC Gas | Generator/Trans | 21.1N, 72.6E | Power Map | Industrial hub
45 | BHARUCH | 220kV | South Gujarat | Bharuch | — | Load/Trans | 21.7N, 73.0E | Power Map
46 | DHUVARAN (DGBPS) | 220kV | South Gujarat | Anand | Dhuvaran CCPP (GSECL) | Generator | 22.3N, 73.0E | Power Map | Gas plant
47 | UTRAN (UGPP) | 220kV | South Gujarat | Surat | Utran CCPP (GSECL) | Generator | 21.2N, 72.9E | Power Map | Gas plant
48 | SUGEN / UNOSUGEN | 220kV | South Gujarat | Surat | Sugen CCPP (Torrent) | Generator | 21.3N, 72.8E | Power Map | 1148+383 MW gas
49 | KAWAS (NTPC) | 220kV | South Gujarat | Surat | Kawas Gas (NTPC) | Generator | 21.3N, 72.9E | Power Map | Central sector gas
50 | JHANOR / GANDHAR (NTPC) | 220kV | South Gujarat | Bharuch | Jhanor-JGPS (NTPC) | Generator | 21.9N, 73.1E | Power Map | Central sector gas

## 14_TRANSMISSION_LINES
GUJARAT TRANSMISSION LINES ¦ Source: GETCO Power Map 01-Sep-2023 ¦ ⚠️ Connectivity identified; R/X/B and MVA limits require GETCO network data
LEGEND from map: Red=400kV ¦ Green=220kV ¦ Blue=132kV ¦ Grey/Black=765kV ¦ Purple=HVDC Bipole ¦ Dashed=Proposed. Thermal limits (MVA), impedances (R/X/B) marked as UNKNOWN — must be sourced from GETCO. Approximate lengths estimated from map scale.
B. TRANSMISSION LINE LIST — From/To connectivity extracted from GETCO Power Map
# | From Bus | To Bus | Voltage (kV) | Approx Length (km) | No. of Circuits | R (pu) ⚠️ Unknown | X (pu) ⚠️ Unknown | Smax (MVA) ⚠️ Unknown | Zone / Corridor | Remarks
1 | KANSARI (NERDA) | RANA (PGCIL) | 765 | 220 | 1 | UNKNOWN | UNKNOWN | UNKNOWN | WR-NR interface | 765kV WR–NR tie; key inter-regional corridor
2 | KANSARI (NERDA) | BANASKANTHA | 765 | 80 | 1 | UNKNOWN | UNKNOWN | UNKNOWN | North Gujarat | New 765kV RE evacuation
3 | KHAVDA-1 (PSTS) | BHUJ (PGCIL) | 765 | 120 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch RE | RE evacuation 765kV
4 | KHAVDA-2 (PSTS) | KANSARI | 765 | 250 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch→North Guj | RE bulk transfer
5 | RANA (PGCIL) | VADODARA | 765 | 120 | 1 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat | 765kV backbone
6 | MUNDRA (HVDC) | MOHINDARGARH (NR) | 500 | 900 | 1 | UNKNOWN | UNKNOWN | 1500 | Kutch→NR HVDC | HVDC bipole; 1,500 MW capacity
7 | BHIMASAR | VANSANA | 400 | 80 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch | Key 400kV Kutch bus
8 | BHIMASAR | BHUJ (PGCIL) | 400 | 60 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch
9 | MUNDRA | BHIMASAR | 400 | 50 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch | Adani/Tata gen to grid
10 | VANSANA | HALVAD | 400 | 90 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch→Saurashtra | Wind evacuation corridor
11 | HALVAD | SURENDRANAGAR | 400 | 70 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
12 | SURENDRANAGAR | RANASAN | 400 | 100 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra→Central
13 | JETPUR | RAJKOT | 400 | 35 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
14 | JETPUR | AMRELI | 400 | 55 | 1 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
15 | JETPUR | BHAVNAGAR | 400 | 80 | 1 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
16 | DEHGAM | RANA (PGCIL) | 400 | 30 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat
17 | DEHGAM | RANASAN | 400 | 40 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat
18 | RANASAN | WANAKBORI | 400 | 35 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat
19 | RANA | VADODARA (PGCIL) | 400 | 100 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Central→South
20 | VADODARA | KASOR | 400 | 15 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat
21 | KASOR | SURAT (PGCIL) | 400 | 90 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | Main south corridor
22 | SURAT | VALSAD | 400 | 60 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | To Maharashtra
23 | BHIMASAR | BHIMASAR_220 | 220 | 0 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch | 220/400 transformer bus
24 | VANSANA | SIKKA | 220 | 70 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch→Saurashtra
25 | VANSANA | JAMNAGAR | 220 | 80 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch
26 | AKRIMOTA | BHIMASAR | 220 | 60 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch | Lignite plant evacuation
27 | VADINAR | SIKKA | 220 | 30 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Kutch | Essar to Sikka
28 | SIKKA | JAMNAGAR | 220 | 25 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
29 | JAMNAGAR | RAJKOT | 220 | 90 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
30 | RAJKOT | MORBI | 220 | 60 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
31 | RAJKOT | WANKANER | 220 | 40 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
32 | RAJKOT | GONDAL | 220 | 35 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
33 | JETPUR | JUNAGADH | 220 | 55 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
34 | AMRELI | BHAVNAGAR | 220 | 65 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra
35 | PIPAVAV | AMRELI | 220 | 55 | 1 | UNKNOWN | UNKNOWN | UNKNOWN | Saurashtra | Gas plant connection
36 | MEHSANA | GANDHINAGAR | 220 | 30 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | North→Central
37 | BANASKANTHA | MEHSANA | 220 | 60 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | North Gujarat
38 | SABARKANTHA | MEHSANA | 220 | 55 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | North Gujarat
39 | PATAN | MEHSANA | 220 | 50 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | North Gujarat
40 | KANSARI | MEHSANA | 220 | 80 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | North Gujarat
41 | CHARANKA | PATAN | 220 | 60 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | North Gujarat | Solar evacuation
42 | GANDHINAGAR | WANAKBORI | 220 | 60 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat | Heavy generation corridor
43 | WANAKBORI | VADODARA | 220 | 65 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | Central→South
44 | WANAKBORI | KADANA | 220 | 50 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat
45 | ANAND | VADODARA | 220 | 40 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat
46 | DEHGAM | GANDHINAGAR | 220 | 15 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat
47 | GANDHINAGAR | RANASAN | 220 | 25 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | Central Gujarat
48 | UKAI | SURAT | 220 | 60 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | Main thermal corridor
49 | UKAI | VADODARA | 220 | 110 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat
50 | SURAT | BHARUCH | 220 | 50 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat
51 | BHARUCH | VADODARA | 220 | 55 | 4 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat
52 | HAZIRA | SURAT | 220 | 15 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | Essar/gas plant to Surat
53 | KAWAS | BHARUCH | 220 | 20 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | NTPC gas
54 | JHANOR | BHARUCH | 220 | 25 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | NTPC gas
55 | UTRAN | SURAT | 220 | 10 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | Gas plant
56 | SUGEN | SURAT | 220 | 15 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | Gas plant
57 | DHUVARAN | ANAND | 220 | 30 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | Gas plant
58 | SURAT | NAVSARI | 220 | 45 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat
59 | NAVSARI | VALSAD | 220 | 35 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | South Gujarat | To Maharashtra
60 | KANSARI | CHITTORGARH (NR) | 765 | 280 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | WR–NR | 765kV NR border
61 | VADODARA | INDORE (WR-PGCIL) | 400 | 250 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | WR backbone | To MP/NR
62 | VALSAD | MUMBAI (PGCIL) | 400 | 180 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | WR–SR border | To Maharashtra/Mumbai
63 | GODHRA | NAGDA (MP) | 220 | 180 | 2 | UNKNOWN | UNKNOWN | UNKNOWN | East Gujarat–MP | To MP border

## 15_ZONAL_MODEL
GUJARAT ZONAL MODEL FOR GAMS ¦ Source: Derived from GETCO Power Map + Installed Capacity ¦ Date: 01-Sep-2023 (Map) / 31-Dec-2025 (Capacity)
This sheet defines the zonal/corridor model for GAMS SCED/SCUC. Since full nodal network data is unavailable, Gujarat is modelled as 5 zones with inter-zonal transfer limits (corridors). Generators and loads are aggregated by zone.
A. ZONE DEFINITIONS
Zone ID | Zone Name | Key Substations | District Coverage | Installed Gen Capacity (MW) | RE Capacity (MW) | Key Load Centres | Congestion Issue | GAMS Set Name
Z1 | Kutch | Mundra, Bhimasar, Bhuj, Khavda, Vansana, Vadinar, Akrimota | Kutch district | APL Mundra 2,640 + CGPL 1,805 + EPGL 1,200 + Akrimota 250 + Panandhro 150 = ~6,045 | Wind ~4,500 + Solar ~3,000 | Bhuj, Gandhidham | HIGH – Generation >> local load; must export via 400kV/765kV/HVDC | KUTCH
Z2 | Saurashtra | Jetpur, Rajkot, Amreli, Bhavnagar, Sikka, Pipavav, Morbi, Jamnagar | Jamnagar, Rajkot, Amreli, Bhavnagar, Junagadh, Porbandar, Morbi, Dwarka | Sikka 500 + GSPC Pipavav 703 = ~1,203 | Wind ~3,500 + Solar ~1,500 | Rajkot, Bhavnagar, Jamnagar | MEDIUM – RE surplus in west Saurashtra; load centres in east | SAURASHTRA
Z3 | North Gujarat | Banaskantha, Mehsana, Patan, Charanka, Kansari, Sabarkantha | Banaskantha, Mehsana, Patan, Sabarkantha, Mahisagar | Minimal thermal | Solar ~5,000 (Charanka + Raghanesda) | Mehsana, Palanpur | HIGH – Solar export zone; 765kV evacuation corridor critical | N_GUJ
Z4 | Central Gujarat | Gandhinagar, Ranasan, Dehgam, Wanakbori, Kadana, Anand, Rana | Gandhinagar, Kheda, Anand, Panchmahal, Dahod | Gandhinagar 630 + Wanakbori 2,270 + Kadana Hy 242 = ~3,142 | Solar ~2,000 | Ahmedabad, Gandhinagar, Anand, Nadiad | MEDIUM – Major thermal zone; also receives from Kutch/North via 400kV | CENTRAL
Z5 | South Gujarat | Ukai, Surat, Bharuch, Hazira, Kawas, Jhanor, Utran, Sugen, Navsari, Valsad | Surat, Bharuch, Narmada, Tapi, Navsari, Valsad, Dang | Ukai TPS 1,110 + Ukai Hy 305 + Dhuvaran 595 + Utran 375 + Sugen 1,148 + Unosugen 383 + Kawas 656 + Jhanor 657 = ~5,229 | Solar ~2,000 | Surat (major), Bharuch, Vapi, Valsad | LOW–MEDIUM – Large thermal + gas base; exporter to Maharashtra via Valsad 400kV | S_GUJ
B. INTER-ZONAL CORRIDORS (for GAMS transfer limits)
Corridor ID | From Zone | To Zone | Voltage | Key Lines | Transfer Limit (MW) ⚠️ Indicative | Direction | Source | Remarks
C1-Z1→Z4 | Z1 Kutch | Z4 Central | 400kV AC | Bhimasar→Halvad→Surendranagar→Ranasan | ~2,000–3,000 | Both | Power Map + WRLDC ATC | Main AC evacuation from Kutch
C2-Z1→EXT | Z1 Kutch | NR (External) | 500kV HVDC | Mundra HVDC Bipole to Mohindargarh | 1,500 | Export only | WRLDC PSP Report | Fixed HVDC schedule; not a GAMS variable
C3-Z1→Z2 | Z1 Kutch | Z2 Saurashtra | 220kV | Vansana→Sikka→Jamnagar | ~800–1,200 | Both | Power Map | Wind farm evacuation
C4-Z3→Z4 | Z3 North | Z4 Central | 765kV+220kV | Kansari→Rana→Ranasan; Mehsana→Gandhinagar | ~1,500–2,000 | Both | Power Map | Solar evacuation + NR interchange
C5-Z2→Z4 | Z2 Saurashtra | Z4 Central | 400kV | Surendranagar→Ranasan | ~1,000–1,500 | Both | Power Map | Saurashtra to central load
C6-Z4→Z5 | Z4 Central | Z5 South | 220kV+400kV | Wanakbori→Vadodara→Kasor→Surat | ~2,000–3,000 | Both | Power Map | Heaviest corridor in state
C7-Z5→MH | Z5 South | Maharashtra | 400kV | Valsad→Mumbai (PGCIL); Surat→BOISAR | ~1,000–1,500 | Both | WRLDC PSP | WR–SR boundary
C8-Z4→MP | Z4 Central | MP (WR) | 220kV | Godhra→Nagda; Vadodara→Indore | ~500–800 | Both | Power Map | East Gujarat to MP/WR
C9-Z3→RJ | Z3 North Gujarat | Rajasthan | 765kV | Kansari→Chittorgarh (NR) | ~1,500 | Both | WRLDC PSP | NR–WR 765kV tie

## 16_CEA_OPERATION_NORMS
CEA OPERATION NORMS — THERMAL POWER STATIONS ¦ Source: CEA Recommendations for CERC Tariff 2024-29 ¦ Published: 2024
Source: CEA Recommendation on Operation Norms (filed with CERC for Tariff Period 2024-29). These are normative values used for tariff determination and GAMS model parameterisation. Station Heat Rate = Gross Station Heat Rate (kcal/kWh). Forced Outage Rate (FOR) = equivalent forced outage rate. Values apply to Gujarat plants unless station-specific data available.
A. NORMATIVE HEAT RATES — Coal/Lignite Units (CEA Norms 2024-29)
# | Plant/Technology Type | Unit Size (MW) | Normative Gross Heat Rate (kcal/kWh) | Design Heat Rate (kcal/kWh) | Normative APC (%) | Normative PLF / PAF (%) | Normative FOR (%) | Min Technical Load (% of MCR) | Technology | Source
1 | Sub-critical Coal | 100–200 MW | 2500 | 2400 | 9 | 85 | 5.5 | 55 | Sub-critical | CEA 2024-29 Norms
2 | Sub-critical Coal | 210 MW (GSECL standard) | 2450 | 2380 | 9 | 85 | 5 | 55 | Sub-critical | CEA 2024-29 Norms
3 | Sub-critical Coal | 250–300 MW | 2425 | 2360 | 8.5 | 85 | 4.5 | 55 | Sub-critical | CEA 2024-29 Norms
4 | Sub-critical Coal | 500 MW | 2375 | 2310 | 8.5 | 85 | 4 | 55 | Sub-critical | CEA 2024-29 Norms
5 | Super-critical Coal | 660 MW | 2340 | 2270 | 8 | 85 | 3.5 | 40 | Super-critical | CEA 2024-29 Norms
6 | Super-critical Coal | 800 MW | 2300 | 2250 | 7.5 | 85 | 3 | 40 | Super-critical | CEA 2024-29 Norms
7 | Lignite (SLPP/Akrimota) | 125 MW | 2850 | 2750 | 10 | 80 | 6 | 55 | Sub-critical Lignite | CEA 2024-29 Norms
8 | CCGT Gas | ~382 MW block | 1900 | 1850 | 3.5 | 80 | 4 | 30 | CCGT | CEA 2024-29 Norms
9 | CCGT Gas | ~1148 MW (Sugen) | 1900 | 1850 | 3.5 | 80 | 4 | 30 | CCGT | CEA 2024-29 Norms
10 | OCGT Gas | 100–250 MW | 2800 | 2700 | 3 | 70 | 6 | 20 | OCGT | CEA 2024-29 Norms
11 | Nuclear (PHWR) | 220 MW | N/A | N/A | 7 | 90 | 2 | Must-run | Nuclear | CEA / NPCIL norms
12 | Nuclear (PHWR) | 700 MW | N/A | N/A | 6.5 | 90 | 2 | Must-run | Nuclear | CEA / NPCIL norms
B. CEA NORMATIVE MIN UP TIME / DOWN TIME — Standard Values (India Practice)
# | Technology | Fuel | Min Up Time (hrs) | Min Down Time (hrs) | Cold Start Time (hrs) | Warm Start (6-48h) | Hot Start (<6h) | Basis | Source | Notes
1 | Sub-critical Coal (210–500 MW) | Coal | 6 | 4 | 8 | 4 | 2 | POSOCO SCED framework / IEA India study | CEA/POSOCO 2023 | Standard for Indian subcritical units
2 | Super-critical Coal (660–800 MW) | Coal | 8 | 6 | 10 | 5 | 2.5 | POSOCO SCED framework | CEA/POSOCO 2023 | Longer ramp; tighter thermal cycling
3 | Lignite (125 MW) | Lignite | 6 | 4 | 10 | 5 | 3 | GSECL/GIPCL operating experience | Proxy | Lignite slower to light off
4 | Gas CCGT (>300 MW) | Gas | 2 | 2 | 4 | 1.5 | 0.5 | IEA CCGT benchmark | IEA/CEA | Fast start capability
5 | Gas OCGT / GT Only | Gas | 0.5 | 0.5 | 1 | 0.5 | 0.25 | IEA OCGT benchmark | IEA | Very fast start
6 | Nuclear PHWR | Nuclear | 72 | 72 | N/A | N/A | N/A | Must-run; no cycling | NPCIL | Cannot be cycled; treat as must-run
7 | Large Hydro (SSP/Ukai/Kadana) | Hydro | 0.1 | 0.1 | 0.5 | 0.1 | 0.05 | IEA hydro benchmark | IEA | Near-instantaneous start

## 17_GETCO_SUBSTATION_LIST
GETCO SUBSTATION LIST — 220/132 kV ¦ Source: GETCO Annexure-A (Scribd) ¦ 116 Substations by Zone/Circle
Source: '08 Annexure-A List of Ss in GETCO System' (Scribd doc 316929944). Lists 116 substations at 220/132kV organised by zone, circle and transmission division. Use alongside Sheet 13 (Network Topology from Power Map). Fault level data (kA, MVA) available separately for impedance proxy calculation.
GETCO 220/132 kV SUBSTATIONS — By Zone (Source: GETCO Annexure-A)
# | Zone | Circle / Division | Substation Name | Voltage (kV) | District | Fault MVA (if known) | Source
1 | Rajkot | Rajkot | Rajkot (220 KV) | 220 | Rajkot | — | GETCO Annexure-A (Scribd)
2 | Rajkot | Rajkot | Wankaner | 220 | Morbi | — | GETCO Annexure-A (Scribd)
3 | Rajkot | Rajkot | Morbi | 220 | Morbi | — | GETCO Annexure-A (Scribd)
4 | Rajkot | Rajkot | Gondal | 220 | Rajkot | — | GETCO Annexure-A (Scribd)
5 | Rajkot | Rajkot | Jetpur | 220 | Rajkot | — | GETCO Annexure-A (Scribd)
6 | Rajkot | Rajkot | Upleta | 220 | Rajkot | — | GETCO Annexure-A (Scribd)
7 | Rajkot | Rajkot | Amreli | 220 | Amreli | — | GETCO Annexure-A (Scribd)
8 | Rajkot | Rajkot | Bhavnagar | 220 | Bhavnagar | — | GETCO Annexure-A (Scribd)
9 | Rajkot | Rajkot | Dhandhuka | 220 | Ahmedabad | — | GETCO Annexure-A (Scribd)
10 | Rajkot | Rajkot | Palitana | 220 | Bhavnagar | — | GETCO Annexure-A (Scribd)
11 | Rajkot | Rajkot | Savarkundla | 220 | Amreli | — | GETCO Annexure-A (Scribd)
12 | Rajkot | Rajkot | Shapur | 220 | Rajkot | — | GETCO Annexure-A (Scribd)
13 | Rajkot | Rajkot | Keshod | 220 | Junagadh | — | GETCO Annexure-A (Scribd)
14 | Rajkot | Rajkot | Junagadh | 220 | Junagadh | — | GETCO Annexure-A (Scribd)
15 | Rajkot | Rajkot | Porbandar | 220 | Porbandar | — | GETCO Annexure-A (Scribd)
16 | Rajkot | Jamnagar | Jamnagar | 220 | Jamnagar | — | GETCO Annexure-A (Scribd)
17 | Rajkot | Jamnagar | Vadinar | 220 | Jamnagar | — | GETCO Annexure-A (Scribd)
18 | Rajkot | Jamnagar | Khambhalia | 220 | Devbhumi Dwarka | — | GETCO Annexure-A (Scribd)
19 | Rajkot | Jamnagar | Dwarka | 220 | Devbhumi Dwarka | — | GETCO Annexure-A (Scribd)
20 | Rajkot | Jamnagar | Okha | 132 | Devbhumi Dwarka | — | GETCO Annexure-A (Scribd)
21 | Rajkot | Jamnagar | Sikka | 220 | Jamnagar | — | GETCO Annexure-A (Scribd)
22 | Bhuj | Bhuj | Bhuj | 220 | Kutch | — | GETCO Annexure-A (Scribd)
23 | Bhuj | Bhuj | Bhimasar | 220 | Kutch | — | GETCO Annexure-A (Scribd)
24 | Bhuj | Bhuj | Vansana | 220 | Kutch | — | GETCO Annexure-A (Scribd)
25 | Bhuj | Bhuj | Ratnal | 220 | Kutch | — | GETCO Annexure-A (Scribd)
26 | Bhuj | Bhuj | Anjar | 220 | Kutch | — | GETCO Annexure-A (Scribd)
27 | Bhuj | Bhuj | Mundra | 220 | Kutch | — | GETCO Annexure-A (Scribd)
28 | Bhuj | Bhuj | Parabada (Panandhro) | 220 | Kutch | — | GETCO Annexure-A (Scribd)
29 | Bhuj | Bhuj | Nakhatrana | 132 | Kutch | — | GETCO Annexure-A (Scribd)
30 | Gandhinagar | Gandhinagar | Gandhinagar (220 KV) | 220 | Gandhinagar | — | GETCO Annexure-A (Scribd)
31 | Gandhinagar | Gandhinagar | Ranasan | 220 | Gandhinagar | — | GETCO Annexure-A (Scribd)
32 | Gandhinagar | Gandhinagar | Dehgam | 220 | Gandhinagar | — | GETCO Annexure-A (Scribd)
33 | Gandhinagar | Gandhinagar | Kadi | 220 | Mehsana | — | GETCO Annexure-A (Scribd)
34 | Gandhinagar | Gandhinagar | Kalol | 132 | Gandhinagar | — | GETCO Annexure-A (Scribd)
35 | Gandhinagar | Ahmedabad | Narol | 220 | Ahmedabad | — | GETCO Annexure-A (Scribd)
36 | Gandhinagar | Ahmedabad | Ghodasar | 220 | Ahmedabad | — | GETCO Annexure-A (Scribd)
37 | Gandhinagar | Ahmedabad | Vatva | 220 | Ahmedabad | — | GETCO Annexure-A (Scribd)
38 | Gandhinagar | Ahmedabad | Chandkheda | 220 | Ahmedabad | — | GETCO Annexure-A (Scribd)
39 | Gandhinagar | Ahmedabad | Odhav | 132 | Ahmedabad | — | GETCO Annexure-A (Scribd)
40 | Mehsana | Mehsana | Mehsana (220 KV) | 220 | Mehsana | — | GETCO Annexure-A (Scribd)
41 | Mehsana | Mehsana | Unjha | 220 | Mehsana | — | GETCO Annexure-A (Scribd)
42 | Mehsana | Mehsana | Visnagar | 132 | Mehsana | — | GETCO Annexure-A (Scribd)
43 | Mehsana | Patan | Patan | 220 | Patan | — | GETCO Annexure-A (Scribd)
44 | Mehsana | Patan | Siddhpur | 220 | Patan | — | GETCO Annexure-A (Scribd)
45 | Mehsana | Patan | Radhanpur | 132 | Patan | — | GETCO Annexure-A (Scribd)
46 | Mehsana | Palanpur | Palanpur | 220 | Banaskantha | — | GETCO Annexure-A (Scribd)
47 | Mehsana | Palanpur | Deesa | 132 | Banaskantha | — | GETCO Annexure-A (Scribd)
48 | Mehsana | Palanpur | Dhanera | 132 | Banaskantha | — | GETCO Annexure-A (Scribd)
49 | Mehsana | Sabarkantha | Himatnagar | 220 | Sabarkantha | — | GETCO Annexure-A (Scribd)
50 | Mehsana | Sabarkantha | Modasa | 220 | Mahisagar | — | GETCO Annexure-A (Scribd)
51 | Mehsana | Sabarkantha | Idar | 132 | Sabarkantha | — | GETCO Annexure-A (Scribd)
52 | Vadodara | Vadodara | Vadodara (Gotri) SLDC | 220 | Vadodara | — | GETCO Annexure-A (Scribd)
53 | Vadodara | Vadodara | Manjusar | 220 | Vadodara | — | GETCO Annexure-A (Scribd)
54 | Vadodara | Vadodara | Wanakbori | 220 | Kheda | — | GETCO Annexure-A (Scribd)
55 | Vadodara | Vadodara | Anand | 220 | Anand | — | GETCO Annexure-A (Scribd)
56 | Vadodara | Vadodara | Nadiad | 220 | Kheda | — | GETCO Annexure-A (Scribd)
57 | Vadodara | Vadodara | Dhuvaran | 220 | Anand | — | GETCO Annexure-A (Scribd)
58 | Vadodara | Vadodara | Karnasad | 220 | Anand | — | GETCO Annexure-A (Scribd)
59 | Vadodara | Vadodara | Godhra | 220 | Panchmahal | — | GETCO Annexure-A (Scribd)
60 | Vadodara | Vadodara | Halol | 220 | Panchmahal | — | GETCO Annexure-A (Scribd)
61 | Vadodara | Vadodara | Dahod | 220 | Dahod | — | GETCO Annexure-A (Scribd)
62 | Vadodara | Vadodara | Lunawada | 132 | Mahisagar | — | GETCO Annexure-A (Scribd)
63 | Vadodara | Vadodara | Kadana | 220 | Mahisagar | — | GETCO Annexure-A (Scribd)
64 | Vadodara | Vadodara | Limkheda | 132 | Dahod | — | GETCO Annexure-A (Scribd)
65 | Surat | Surat | Surat (Sachin) | 220 | Surat | — | GETCO Annexure-A (Scribd)
66 | Surat | Surat | Hazira | 220 | Surat | — | GETCO Annexure-A (Scribd)
67 | Surat | Surat | Bardoli | 220 | Surat | — | GETCO Annexure-A (Scribd)
68 | Surat | Surat | Vapi | 220 | Valsad | — | GETCO Annexure-A (Scribd)
69 | Surat | Surat | Navsari | 220 | Navsari | — | GETCO Annexure-A (Scribd)
70 | Surat | Surat | Bilimora | 132 | Navsari | — | GETCO Annexure-A (Scribd)
71 | Surat | Bharuch | Bharuch | 220 | Bharuch | — | GETCO Annexure-A (Scribd)
72 | Surat | Bharuch | Kawas | 220 | Surat | — | GETCO Annexure-A (Scribd)
73 | Surat | Bharuch | Ankleshwar | 220 | Bharuch | — | GETCO Annexure-A (Scribd)
74 | Surat | Bharuch | Kosamba | 220 | Surat | — | GETCO Annexure-A (Scribd)
75 | Surat | Bharuch | Ukai | 220 | Tapi | — | GETCO Annexure-A (Scribd)
76 | Surat | Bharuch | Vyara | 132 | Tapi | — | GETCO Annexure-A (Scribd)
77 | Surat | Bharuch | Mandvi Surat | 220 | Surat | — | GETCO Annexure-A (Scribd)
78 | Surat | Junagadh | Veraval | 132 | Gir Somnath | — | GETCO Annexure-A (Scribd)
79 | Surat | Junagadh | Una | 132 | Gir Somnath | — | GETCO Annexure-A (Scribd)
80 | Surat | Junagadh | Talala | 132 | Gir Somnath | — | GETCO Annexure-A (Scribd)
81 | Surat | Junagadh | Pipavav | 220 | Amreli | — | GETCO Annexure-A (Scribd)
82 | Surat | Junagadh | Khambhat | 220 | Anand | — | GETCO Annexure-A (Scribd)

## 18_OUTAGE_FRAMEWORK
UNIT OUTAGE FRAMEWORK & AVAILABILITY ¦ Source: NPP DGR Reports + CEA Performance Norms ¦ Date: Jun-2026
Source: National Power Portal (npp.gov.in) DGR-10 Daily Outage Report structure + CEA normative FOR values. NPP publishes daily unit-wise outage data but direct download requires portal access. This sheet provides the framework with CEA normative forced outage rates (FOR%) for GAMS unit availability modelling. RECOMMENDED: Download DGR-10 XLS daily from npp.gov.in/publishedReports for actual availability flags.
A. CEA NORMATIVE FORCED OUTAGE & AVAILABILITY — Gujarat Thermal Units
# | Station | Unit | Fuel | Installed (MW) | Normative PAF (%) | Normative FOR (%) | Normative PLF (%) | GAMS Availability Parameter | NPP Download URL
1 | GANDHINAGAR TPS | 3 | Coal | 210 | 85 | 5 | 65 | u_avail[GTPS,3,t] ∈ {0,1} | npp.gov.in DGR-10
2 | GANDHINAGAR TPS | 4 | Coal | 210 | 85 | 5 | 65 | u_avail[GTPS,4,t] ∈ {0,1} | npp.gov.in DGR-10
3 | GANDHINAGAR TPS | 5 | Coal | 210 | 85 | 4.5 | 68 | u_avail[GTPS,5,t] ∈ {0,1} | npp.gov.in DGR-10
4 | WANAKBORI TPS | 1-6 | Coal | 210 | 85 | 5 | 70 | u_avail[WTPS,1-6,t] ∈ {0,1} | npp.gov.in DGR-10
5 | WANAKBORI TPS | 7 | Coal | 210 | 85 | 5 | 70 | u_avail[WTPS,7,t] ∈ {0,1} | npp.gov.in DGR-10
6 | UKAI TPS | 1-2 | Coal | 120 | 80 | 7 | 55 | u_avail[UKAI,1-2,t] ∈ {0,1} | npp.gov.in DGR-10
7 | UKAI TPS | 3-5 | Coal | 200 | 83 | 5.5 | 62 | u_avail[UKAI,3-5,t] ∈ {0,1} | npp.gov.in DGR-10
8 | UKAI TPS | 6 | Coal | 500 | 85 | 4 | 72 | u_avail[UKAI,6,t] ∈ {0,1} | npp.gov.in DGR-10
9 | SIKKA TPS | 3-4 | Coal | 250 | 82 | 6 | 58 | u_avail[SIKKA,3-4,t] ∈ {0,1} | npp.gov.in DGR-10
10 | APL MUNDRA Stage-1 | 1-4 | Coal | 330 | 88 | 3.5 | 75 | u_avail[APL1,1-4,t] ∈ {0,1} | npp.gov.in DGR-10
11 | APL MUNDRA Stage-2 | 1-2 | Coal | 660 | 88 | 3 | 78 | u_avail[APL2,1-2,t] ∈ {0,1} | npp.gov.in DGR-10
12 | EPGL (Essar Vadinar) | 1-2 | Coal | 600 | 87 | 3.5 | 74 | u_avail[EPGL,1-2,t] ∈ {0,1} | npp.gov.in DGR-10
13 | CGPL MUNDRA UMPP | 1-5 | Coal | 830 | 88 | 3 | 75 | u_avail[CGPL,1-5,t] ∈ {0,1} | npp.gov.in DGR-10
14 | SLPP (GIPCL) | 1-4 | Lignite | 125 | 80 | 6 | 65 | u_avail[SLPP,1-4,t] ∈ {0,1} | npp.gov.in DGR-10
15 | AKRIMOTA (BECL) | 1-2 | Lignite | 125 | 78 | 7 | 60 | u_avail[AKRIM,1-2,t] ∈ {0,1} | npp.gov.in DGR-10
16 | SUGEN CCPP | Full | Gas | 1148 | 80 | 4 | 45 | u_avail[SUGEN,t] ∈ {0,1} | npp.gov.in DGR-10
17 | UNOSUGEN | Full | Gas | 383 | 80 | 4 | 40 | u_avail[UNSUG,t] ∈ {0,1} | npp.gov.in DGR-10
18 | DHUVARAN CCPP | Full | Gas | 595 | 75 | 5 | 35 | u_avail[DHUV,t] ∈ {0,1} | npp.gov.in DGR-10
19 | UTRAN CCPP | Full | Gas | 375 | 75 | 5 | 30 | u_avail[UTRAN,t] ∈ {0,1} | npp.gov.in DGR-10
20 | SIPAT-I (NTPC) | 1-3 | Coal | 660 | 90 | 3 | 80 | u_avail[SIP1,1-3,t] ∈ {0,1} | npp.gov.in DGR-10
21 | SIPAT-II (NTPC) | 1-2 | Coal | 500 | 90 | 3 | 80 | u_avail[SIP2,1-2,t] ∈ {0,1} | npp.gov.in DGR-10
22 | VSTPS I–V (NTPC) | Various | Coal | 210/500 | 90 | 3 | 78 | u_avail[VSTPS,t] ∈ {0,1} | npp.gov.in DGR-10
23 | KAPS 1&2 (Nuclear) | 1-2 | Nuclear | 220 | 90 | 2 | Must-run | u_avail[KAPS,t]=1 (must-run) | Must-run; no outage
24 | KAPS 3&4 (Nuclear) | 1-2 | Nuclear | 700 | 90 | 2 | Must-run | u_avail[KAPS34,t]=1 (must-run) | Must-run; no outage
25 | TARAPUR 1-4 (Nuclear) | 1-4 | Nuclear | 160/540 | 90 | 2 | Must-run | u_avail[TAPS,t]=1 (must-run) | Must-run; no outage
B. NPP DAILY OUTAGE REPORT — HOW TO DOWNLOAD (Manual Process Required)
Step 1 | Go to: https://npp.gov.in/publishedReports
Step 2 | Under 'Daily Generation Reports' → Click DGR-10 XLS (Coal/Lignite/Nuclear Outage Report)
Step 3 | Filter by State = Gujarat or search for Gujarat plant names
Step 4 | Column structure: Station ¦ Unit ¦ Capacity ¦ Outage Type ¦ Start Date ¦ Expected Return
Step 5 | DGR-12 = Units out >15 days (long-term outage); DGR-15 = Units went out today
Step 6 | Map outage dates to 96-block availability flags for GAMS model input
Note | NPP blocks direct download from automated scripts; must be downloaded manually from browser

## 19_SPINNING_RESERVE
SPINNING RESERVE & ANCILLARY SERVICES FRAMEWORK — GUJARAT ¦ Source: GERC BESS Reg 2026 + IEGC + CERC AS Framework
Sources: (1) GERC Grid Interactive BESS Regulations 2026 (notified May 2026) — SLDC empowered to dispatch ancillary services. (2) IEGC 5th Amendment — frequency response obligation for WR states. (3) CERC Ancillary Services Regulations 2022 — framework for spinning reserve, regulation reserve, black start. Exact MW quantum for Gujarat spinning reserve not publicly notified; values below are IEGC-derived estimates.
A. SPINNING RESERVE OBLIGATION — Gujarat (IEGC-derived Estimates)
Parameter | Value / Requirement | Basis | GAMS Model Constraint | Source | Status | Remarks
Primary Reserve (Frequency Response) | ≥ 5% of peak demand online | IEGC — all constituents must maintain 5% primary reserve | ∑ P_online(t) ≥ P_demand(t) × 1.05 | IEGC 5th Amendment | ⚠️ Estimated | Apply to all online thermal units
Secondary Reserve (Regulation) | ≥ 2–3% of peak demand | CERC AS Regulations 2022 — regulation reserve band | ∑ headroom(t) ≥ P_demand(t) × 0.025 | CERC AS Reg 2022 | ⚠️ Estimated | Gas plants preferred for fast regulation
Gujarat Peak Demand (30-May-2026) | 26,093 MW (max of day) | WRLDC PSP 30-May-2026 (Sheet 10) | P_demand_peak = 26,093 MW | WRLDC PSP | ✅ Actual | Use for reserve sizing
Gujarat Evening Peak (typical) | 22,000–24,000 MW | WRLDC PSP historical range (Sheet 10) | P_demand_eve = 22,000–24,000 MW | WRLDC PSP | ✅ Actual
Implied Primary Reserve Requirement | ~1,100–1,300 MW (5% of 22,000–26,000 MW) | IEGC 5% rule applied to Gujarat peak | SR_min(t) ≥ 0.05 × Load(t) | Derived | ⚠️ Proxy | Confirm with SLDC
Implied Regulation Reserve | ~550–650 MW (2.5% of peak) | CERC 2.5% regulation band | Reg_min(t) ≥ 0.025 × Load(t) | Derived | ⚠️ Proxy | BESS now eligible per GERC 2026
BESS for Ancillary Services | Eligible from 2026 | GERC BESS Reg 2026 — SLDC to dispatch BESS for AS | Add BESS as AS provider in model | GERC BESS Reg 2026 | ✅ Confirmed | Key new development
Must-Run Units (Nuclear + SSP) | ~1,400 MW always online | Nuclear + SSP = must-run per Grid Code | u_commit[nuclear,t] = 1 for all t | Grid Code / SLDC | ✅ Confirmed | Cannot be committed off
Frequency Response Obligation (FRO) | Assessed annually per RLDC | CERC Methodology for FRO computation — NLDC circular 2024 | FRO constraint in UC formulation | NLDC Circular 2024 | ✅ Framework | Gujarat FRO quantum from WRLDC
B. ANCILLARY SERVICE TYPES — GERC Framework 2026
Service Type | Response Time | Duration | Provider Eligible | GAMS Constraint | GERC 2026 Status
Primary Frequency Response | < 10 seconds | 30 min | Thermal (online), Hydro, BESS | droop_response ≥ FRO_obligation | Eligible: All online generators
Secondary Regulation (AGC) | < 30 seconds | Continuous | Gas CCGT, Hydro, BESS | AGC_band = ±regulation_reserve | BESS newly eligible per GERC 2026
Spinning Reserve | < 10 minutes | 30 min | Online thermal headroom, Hydro | ∑headroom ≥ SR_min(t) | Thermal headroom + Hydro
Non-Spinning Reserve | < 30 minutes | 60 min | Fast-start gas GT, BESS | OCGT start within 30 min | Gas GTs at Kawas, Jhanor
Black Start | < 4 hours | — | Designated units only | Exogenous; not in UC | Designated by SLDC separately
Peak Management | Day-ahead | Hours | BESS, Hydro, Gas peakers | Peaking_unit binary in UC | GERC BESS 2026 permits
Energy Arbitrage (BESS) | Day-ahead | Hours | Standalone BESS | Charge/discharge in off-peak/peak | GERC BESS 2026 permits

## 20_DATA_SOURCES_REGISTER
EXTERNAL DATA SOURCES REGISTER ¦ All public sources identified for Gujarat SCED/SCUC model ¦ Updated: Jun-2026
# | Data Parameter | Source Name | URL / Reference | Format | Access | Data Freshness | Sheet in This File
1 | Installed Capacity | GETCO/SLDC | Installed_capacity_311225 PDF (uploaded) | PDF | Direct upload | 31-Dec-2025 | 1_INSTALLED_CAP
2 | Technical Minimum (Pmin) | SLDC Vadodara | TECHNICAL_MINIMUM.pdf (uploaded) | PDF | Direct upload | Current | 2_TECH_MINIMUM
3 | Merit Order (Variable Cost) | SLDC MOD | MOSLDC02062620260603054336.pdf (uploaded) | PDF | Direct upload | 02-Jun-2026 | 3_MERIT_ORDER_VAR
4 | Full Merit Order + Schedule | SLDC MOS Excel | MeritOrderSummary_GJT_30_May_2026.xlsx (uploaded) | XLS | Direct upload | 30-May to 03-Jun-2026 | 4_MERIT_ORDER_FULL
5 | Coal Supply Curve (India) | ICED / NITI Aayog | iced-power-supply-curve-india-coal-2024-25.csv (uploaded) | CSV | Direct upload | 2024-25 | 5_COAL_SUPPLY_CURVE
6 | Ramp Rates (proxy) | CEA/CERC Regulations 2023 | cercind.gov.in/regulations | PDF | Public | 2023 | 6_RAMP_RATES
7 | Gujarat Actual Generation | WRLDC / Grid-India | WRLDC_PSP_Report_30-05-2026.pdf (uploaded) | PDF | Direct upload | 30-May-2026 | 8_GUJ_ACTUAL_GEN
8 | ISGS Drawal Schedule | WRLDC / Grid-India | WRLDC_PSP_Report_30-05-2026.pdf (uploaded) | PDF | Direct upload | 30-May-2026 | 9_ISGS_DRAWAL
9 | Gujarat Demand + RE Curtailment | WRLDC / Grid-India | WRLDC_PSP_Report_30-05-2026.pdf (uploaded) | PDF | Direct upload | 30-May-2026 | 10_GUJ_DEMAND_CURT
10 | Reservoir Levels | WRLDC / Grid-India | WRLDC_PSP_Report_30-05-2026.pdf (uploaded) | PDF | Direct upload | 30-May-2026 | 11_RESERVOIR_LEVELS
11 | IR Exchange + Frequency | WRLDC / Grid-India | WRLDC_PSP_Report_30-05-2026.pdf (uploaded) | PDF | Direct upload | 30-May-2026 | 12_IR_EXCHANGE
12 | Network Bus Topology | GETCO | Gujarat_Power_Map_01_09_2023.pdf (uploaded) | PDF Map | Direct upload | 01-Sep-2023 | 13_NETWORK_TOPOLOGY
13 | Transmission Line Connectivity | GETCO | Gujarat_Power_Map_01_09_2023.pdf (uploaded) | PDF Map | Direct upload | 01-Sep-2023 | 14_TRANSMISSION_LINES
14 | Zonal Model (5-zone) | Derived | Derived from Power Map + Installed Capacity | Derived | Internal | 2023/2025 | 15_ZONAL_MODEL
15 | CEA Operation Norms (Heat Rate, FOR, MUT) | CEA / CERC | cercind.gov.in/2024/draft_reg/TTF2024/CEA-Recommendation on Operation Norms.pdf | PDF | Public | 2024 | 16_CEA_OPERATION_NORMS
16 | GETCO 220/132kV Substation List | GETCO (via Scribd) | scribd.com/doc/316929944/08-Annexure-a-List-of-Ss-in-GETCO-System | PDF | Public (Scribd) | 2016 (needs update) | 17_GETCO_SUBSTATION_LIST
17 | GETCO Fault Level Data (220kV) | GETCO (via Scribd) | scribd.com/document/595220041/Fault-level-Dec-2021 | PDF | Public (Scribd) | Dec-2021 | Use to derive impedance proxy
18 | Daily Outage Report (DGR-10) | CEA / NPP | npp.gov.in/publishedReports → DGR-10 XLS | XLS | Public (manual download) | Daily | 18_OUTAGE_FRAMEWORK
19 | Monthly Station Generation | CEA / NPP | npp.gov.in/publishedReports → Monthly 18-col Report | XLS | Public (manual download) | Monthly | Cross-validation
20 | Spinning Reserve / AS Framework | GERC / CERC | gercin.org/wp-content/uploads/2026/05/Final_DRAFT-BESS-REGULATION-GERC.pdf | PDF | Public | May-2026 | 19_SPINNING_RESERVE
21 | Hourly Load Profile (Gujarat) | ICED / NITI Aayog | iced.niti.gov.in/energy/electricity/distribution/national-level-consumption/load-curve | Web (interactive) | Public (scrape) | Up to Mar-2026 | Not yet extracted — manual scrape needed
22 | 96-block Demand Data (actual) | SLDC Gujarat | sldcguj.com (login required) | App/Portal | Login required | Real-time | ❌ Requires SLDC access
23 | RE Forecast 15-min profile | SLDC REMC | Internal SLDC system | Internal | SLDC internal | Daily | ❌ Requires SLDC access
24 | Line Impedances R/X/B | GETCO Network Planning | Internal GETCO network model | Internal | GETCO internal | Current | ❌ Requires GETCO access
25 | Gas Nomination Daily | GAIL / GSPC | Internal GAIL nominations | Internal | Utility internal | Daily | ❌ Requires GAIL/GSPC access

## 21_LOAD_PROFILE_96BLK
GUJARAT 96-BLOCK LOAD PROFILE ¦ 🔴 REPRODUCED from WRLDC PSP + seasonal shape ¦ Verify with SLDC
DATA AUTHENTICITY: 🟢 AUTH = Official source / uploaded doc ¦ 🟡 DERIV = Calculated from authentic data ¦ 🟠 PROXY = Regulatory norm (CEA/CERC/IEA) — valid but not unit-specific ¦ 🔴 REPR = Reproduced by engineering judgment — MUST BE VERIFIED before GAMS use THIS SHEET: Reproduced using WRLDC PSP 30-May-2026 anchors (peak=22,145 MW @20:00; trough=20,185 MW @03:00; max=26,093 MW @15:30; solar peak=9,993 MW @12:08; wind avg=5,181 MW). Seasonal shapes derived from typical Gujarat demand patterns. Values are ESTIMATES.
Blk | Time | SumWkDay (MW) | SumWkEnd (MW) | Winter WkDay(MW) | Monsoon WkDay(MW) | Solar 30-May(MW) | Wind 30-May(MW) | Residual Load(MW) | Data Type | Basis
1 | 00:00 | 20091 | 18905 | 17418 | 17905 | 0 | 4999 | 15092 | 🔴 REPR | Seasonal shape model
2 | 00:15 | 20050 | 18869 | 17388 | 17869 | 0 | 4999 | 15051 | 🔴 REPR | Seasonal shape model
3 | 00:30 | 20000 | 18825 | 17350 | 17825 | 0 | 4999 | 15001 | 🔴 REPR | Seasonal shape model
4 | 00:45 | 19940 | 18772 | 17305 | 17772 | 0 | 4999 | 14941 | 🔴 REPR | Seasonal shape model
5 | 01:00 | 19871 | 18712 | 17253 | 17712 | 0 | 4999 | 14872 | 🔴 REPR | Seasonal shape model
6 | 01:15 | 19794 | 18645 | 17196 | 17645 | 0 | 4999 | 14795 | 🔴 REPR | Seasonal shape model
7 | 01:30 | 19714 | 18575 | 17136 | 17575 | 0 | 4998 | 14716 | 🔴 REPR | Seasonal shape model
8 | 01:45 | 19634 | 18505 | 17076 | 17505 | 0 | 4998 | 14636 | 🔴 REPR | Seasonal shape model
9 | 02:00 | 19559 | 18440 | 17019 | 17439 | 0 | 4997 | 14562 | 🔴 REPR | Seasonal shape model
10 | 02:15 | 19494 | 18383 | 16970 | 17382 | 0 | 4997 | 14497 | 🔴 REPR | Seasonal shape model
11 | 02:30 | 19443 | 18339 | 16932 | 17338 | 0 | 4996 | 14447 | 🔴 REPR | Seasonal shape model
12 | 02:45 | 19411 | 18312 | 16908 | 17310 | 0 | 4994 | 14417 | 🔴 REPR | Seasonal shape model
13 | 03:00 | 19400 | 18304 | 16900 | 17300 | 0 | 4993 | 14407 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
14 | 03:15 | 19411 | 18316 | 16908 | 17311 | 0 | 4990 | 14421 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
15 | 03:30 | 19444 | 18348 | 16933 | 17340 | 0 | 4988 | 14456 | 🔴 REPR | Seasonal shape model
16 | 03:45 | 19495 | 18397 | 16971 | 17387 | 0 | 4984 | 14511 | 🔴 REPR | Seasonal shape model
17 | 04:00 | 19562 | 18461 | 17022 | 17449 | 0 | 4980 | 14582 | 🔴 REPR | Seasonal shape model
18 | 04:15 | 19640 | 18537 | 17082 | 17521 | 0 | 4974 | 14666 | 🔴 REPR | Seasonal shape model
19 | 04:30 | 19725 | 18621 | 17149 | 17603 | 0 | 4967 | 14758 | 🔴 REPR | Seasonal shape model
20 | 04:45 | 19813 | 18709 | 17222 | 17690 | 0 | 4958 | 14855 | 🔴 REPR | Seasonal shape model
21 | 05:00 | 19902 | 18800 | 17303 | 17783 | 0 | 4948 | 14954 | 🔴 REPR | Seasonal shape model
22 | 05:15 | 19990 | 18891 | 17394 | 17882 | 0 | 4936 | 15054 | 🔴 REPR | Seasonal shape model
23 | 05:30 | 20080 | 18984 | 17504 | 17989 | 0 | 4920 | 15160 | 🔴 REPR | Seasonal shape model
24 | 05:45 | 20174 | 19078 | 17641 | 18108 | 0 | 4902 | 15272 | 🔴 REPR | Seasonal shape model
25 | 06:00 | 20275 | 19175 | 17818 | 18243 | 909 | 4881 | 14485 | 🔴 REPR | Seasonal shape model
26 | 06:15 | 20391 | 19277 | 18046 | 18398 | 1101 | 4856 | 14434 | 🔴 REPR | Seasonal shape model
27 | 06:30 | 20526 | 19386 | 18333 | 18577 | 1323 | 4827 | 14376 | 🔴 REPR | Seasonal shape model
28 | 06:45 | 20686 | 19503 | 18682 | 18780 | 1577 | 4794 | 14315 | 🔴 REPR | Seasonal shape model
29 | 07:00 | 20875 | 19629 | 19085 | 19007 | 1865 | 4756 | 14254 | 🔴 REPR | Seasonal shape model
30 | 07:15 | 21094 | 19764 | 19523 | 19253 | 2188 | 4713 | 14193 | 🔴 REPR | Seasonal shape model
31 | 07:30 | 21342 | 19907 | 19966 | 19508 | 2546 | 4664 | 14132 | 🔴 REPR | Seasonal shape model
32 | 07:45 | 21612 | 20057 | 20375 | 19761 | 2939 | 4610 | 14063 | 🔴 REPR | Seasonal shape model
33 | 08:00 | 21895 | 20210 | 20706 | 19999 | 3367 | 4551 | 13977 | 🔴 REPR | Seasonal shape model
34 | 08:15 | 22176 | 20362 | 20923 | 20204 | 3825 | 4486 | 13865 | 🔴 REPR | Seasonal shape model
35 | 08:30 | 22440 | 20508 | 20999 | 20364 | 4312 | 4415 | 13713 | 🔴 REPR | Seasonal shape model
36 | 08:45 | 22669 | 20644 | 20924 | 20465 | 4822 | 4340 | 13507 | 🔴 REPR | Seasonal shape model
37 | 09:00 | 22845 | 20764 | 20708 | 20499 | 5349 | 4259 | 13237 | 🔴 REPR | Seasonal shape model
38 | 09:15 | 22955 | 20864 | 20378 | 20465 | 5887 | 4175 | 12893 | 🔴 REPR | Seasonal shape model
39 | 09:30 | 22986 | 20938 | 19973 | 20364 | 6428 | 4088 | 12470 | 🔴 REPR | Seasonal shape model
40 | 09:45 | 22933 | 20984 | 19534 | 20206 | 6963 | 3999 | 11971 | 🔴 REPR | Seasonal shape model
41 | 10:00 | 22795 | 20999 | 19102 | 20001 | 7482 | 3908 | 11405 | 🔴 REPR | Seasonal shape model
42 | 10:15 | 22575 | 20984 | 18708 | 19766 | 7976 | 3817 | 10782 | 🔴 REPR | Seasonal shape model
43 | 10:30 | 22279 | 20938 | 18372 | 19516 | 8435 | 3728 | 10116 | 🔴 REPR | Seasonal shape model
44 | 10:45 | 21919 | 20864 | 18103 | 19265 | 8850 | 3641 | 9428 | 🔴 REPR | Seasonal shape model
45 | 11:00 | 21508 | 20764 | 17899 | 19027 | 9211 | 3558 | 8739 | 🔴 REPR | Seasonal shape model
46 | 11:15 | 21068 | 20645 | 17753 | 18811 | 9511 | 3481 | 8076 | 🔴 REPR | Seasonal shape model
47 | 11:30 | 20623 | 20509 | 17653 | 18623 | 9743 | 3411 | 7469 | 🔴 REPR | Seasonal shape model
48 | 11:45 | 20203 | 20363 | 17589 | 18465 | 9901 | 3349 | 6953 | 🔴 REPR | Seasonal shape model
49 | 12:00 | 19839 | 20213 | 17549 | 18338 | 9982 | 3297 | 6560 | 🔴 REPR | Seasonal shape model
50 | 12:15 | 19558 | 20062 | 17526 | 18239 | 9983 | 3255 | 6320 | 🔴 REPR | Seasonal shape model
51 | 12:30 | 19378 | 19915 | 17513 | 18164 | 9906 | 3225 | 6247 | 🔴 REPR | Seasonal shape model
52 | 12:45 | 19304 | 19777 | 17506 | 18109 | 9750 | 3206 | 6348 | 🔴 REPR | Seasonal shape model
53 | 13:00 | 19325 | 19649 | 17503 | 18071 | 9522 | 3201 | 6602 | 🔴 REPR | Seasonal shape model
54 | 13:15 | 19417 | 19534 | 17501 | 18045 | 9224 | 3207 | 6986 | 🔴 REPR | Seasonal shape model
55 | 13:30 | 19552 | 19432 | 17500 | 18027 | 8865 | 3227 | 7460 | 🔴 REPR | Seasonal shape model
56 | 13:45 | 19701 | 19345 | 17500 | 18016 | 8452 | 3259 | 7990 | 🔴 REPR | Seasonal shape model
57 | 14:00 | 19841 | 19271 | 17500 | 18009 | 7995 | 3303 | 8543 | 🔴 REPR | Seasonal shape model
58 | 14:15 | 19959 | 19211 | 17500 | 18005 | 7502 | 3358 | 9099 | 🔴 REPR | Seasonal shape model
59 | 14:30 | 20048 | 19163 | 17500 | 18003 | 6984 | 3424 | 9640 | 🔴 REPR | Seasonal shape model
60 | 14:45 | 20110 | 19126 | 17500 | 18001 | 6450 | 3500 | 10160 | 🔴 REPR | Seasonal shape model
61 | 15:00 | 20151 | 19101 | 17500 | 18001 | 5909 | 3586 | 10656 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
62 | 15:15 | 20176 | 19087 | 17500 | 18001 | 5371 | 3679 | 11126 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
63 | 15:30 | 20191 | 19084 | 17501 | 18003 | 4843 | 3780 | 11568 | 🔴 REPR | Seasonal shape model
64 | 15:45 | 20202 | 19095 | 17503 | 18007 | 4332 | 3888 | 11982 | 🔴 REPR | Seasonal shape model
65 | 16:00 | 20213 | 19122 | 17509 | 18014 | 3844 | 4003 | 12366 | 🔴 REPR | Seasonal shape model
66 | 16:15 | 20230 | 19168 | 17522 | 18028 | 3384 | 4124 | 12722 | 🔴 REPR | Seasonal shape model
67 | 16:30 | 20259 | 19240 | 17549 | 18054 | 2956 | 4250 | 13053 | 🔴 REPR | Seasonal shape model
68 | 16:45 | 20307 | 19341 | 17602 | 18097 | 2561 | 4382 | 13364 | 🔴 REPR | Seasonal shape model
69 | 17:00 | 20384 | 19478 | 17697 | 18166 | 2201 | 4519 | 13664 | 🔴 REPR | Seasonal shape model
70 | 17:15 | 20503 | 19654 | 17858 | 18275 | 1877 | 4660 | 13966 | 🔴 REPR | Seasonal shape model
71 | 17:30 | 20679 | 19874 | 18109 | 18433 | 1588 | 4805 | 14286 | 🔴 REPR | Seasonal shape model
72 | 17:45 | 20924 | 20137 | 18473 | 18655 | 1333 | 4952 | 14639 | 🔴 REPR | Seasonal shape model
73 | 18:00 | 21247 | 20439 | 18960 | 18947 | 1110 | 5100 | 15037 | 🔴 REPR | Seasonal shape model
74 | 18:15 | 21650 | 20772 | 19560 | 19312 | 916 | 5248 | 15486 | 🔴 REPR | Seasonal shape model
75 | 18:30 | 22122 | 21123 | 20229 | 19739 | 751 | 5392 | 15979 | 🔴 REPR | Seasonal shape model
76 | 18:45 | 22641 | 21473 | 20896 | 20208 | 0 | 5531 | 17110 | 🔴 REPR | Seasonal shape model
77 | 19:00 | 23167 | 21802 | 21471 | 20685 | 0 | 5662 | 17505 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
78 | 19:15 | 23654 | 22088 | 21861 | 21125 | 0 | 5781 | 17873 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
79 | 19:30 | 24050 | 22310 | 22000 | 21484 | 0 | 5886 | 18164 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
80 | 19:45 | 24309 | 22451 | 21861 | 21718 | 0 | 5975 | 18334 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
81 | 20:00 | 24400 | 22500 | 21471 | 21800 | 0 | 6044 | 18356 | 🔴 REPR | Seasonal shape model
82 | 20:15 | 24309 | 22451 | 20896 | 21718 | 0 | 6093 | 18216 | 🔴 REPR | Seasonal shape model
83 | 20:30 | 24050 | 22310 | 20229 | 21484 | 0 | 6120 | 17930 | 🔴 REPR | Seasonal shape model
84 | 20:45 | 23654 | 22088 | 19560 | 21125 | 0 | 6126 | 17528 | 🔴 REPR | Seasonal shape model
85 | 21:00 | 23167 | 21802 | 18960 | 20685 | 0 | 6111 | 17056 | 🔴 REPR | Seasonal shape model
86 | 21:15 | 22641 | 21473 | 18473 | 20208 | 0 | 6077 | 16564 | 🔴 REPR | Seasonal shape model
87 | 21:30 | 22122 | 21122 | 18109 | 19739 | 0 | 6026 | 16096 | 🔴 REPR | Seasonal shape model
88 | 21:45 | 21650 | 20772 | 17858 | 19312 | 0 | 5961 | 15689 | 🔴 REPR | Seasonal shape model
89 | 22:00 | 21247 | 20438 | 17697 | 18947 | 0 | 5885 | 15362 | 🔴 REPR | Seasonal shape model
90 | 22:15 | 20924 | 20136 | 17602 | 18655 | 0 | 5802 | 15122 | 🔴 REPR | Seasonal shape model
91 | 22:30 | 20679 | 19872 | 17549 | 18433 | 0 | 5715 | 14964 | 🔴 REPR | Seasonal shape model
92 | 22:45 | 20503 | 19651 | 17522 | 18275 | 0 | 5628 | 14875 | 🔴 REPR | Seasonal shape model
93 | 23:00 | 20384 | 19473 | 17509 | 18166 | 0 | 5542 | 14842 | 🔴 REPR | Seasonal shape model
94 | 23:15 | 20307 | 19334 | 17503 | 18097 | 0 | 5461 | 14846 | 🔴 REPR | Seasonal shape model
95 | 23:30 | 20259 | 19230 | 17501 | 18054 | 0 | 5385 | 14874 | 🔴 REPR | Seasonal shape model
96 | 23:45 | 20231 | 19153 | 17500 | 18028 | 0 | 5317 | 14914 | 🔴 REPR | Seasonal shape model

## 22_RE_GEN_PROFILE
GUJARAT RE GENERATION PROFILE (96-block) ¦ 🔴 REPRODUCED ¦ Verify with SLDC REMC
DATA AUTHENTICITY: 🟢 AUTH = Official source / uploaded doc ¦ 🟡 DERIV = Calculated from authentic data ¦ 🟠 PROXY = Regulatory norm (CEA/CERC/IEA) — valid but not unit-specific ¦ 🔴 REPR = Reproduced by engineering judgment — MUST BE VERIFIED before GAMS use THIS SHEET: Solar profile from Gaussian clear-sky model anchored to WRLDC PSP (peak 9,993 MW @12:08, day energy 75.73 MU). Wind from WRLDC PSP (peak 6,153 MW @20:06, avg 5,181 MW, day energy 124.34 MU). Zone splits from installed capacity ratios: Solar — Kutch 18%, N.Guj 35%, Central 25%, South 22%; Wind — Kutch 45%, Saurashtra 40%, Others 15%.
Blk | Time | Solar Total (MW) | Wind Total (MW) | Solar:Kutch (MW) | Solar:N.Guj (MW) | Solar:Central (MW) | Solar:South (MW) | Wind:Kutch (MW) | Wind:Saur (MW) | Data Type | Basis
1 | 00:00 | 0 | 4999 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
2 | 00:15 | 0 | 4999 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
3 | 00:30 | 0 | 4999 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
4 | 00:45 | 0 | 4999 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
5 | 01:00 | 0 | 4999 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
6 | 01:15 | 0 | 4999 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
7 | 01:30 | 0 | 4998 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
8 | 01:45 | 0 | 4998 | 0 | 0 | 0 | 0 | 2249 | 1999 | 🔴 REPR | Gaussian solar + diurnal wind model
9 | 02:00 | 0 | 4997 | 0 | 0 | 0 | 0 | 2248 | 1998 | 🔴 REPR | Gaussian solar + diurnal wind model
10 | 02:15 | 0 | 4997 | 0 | 0 | 0 | 0 | 2248 | 1998 | 🔴 REPR | Gaussian solar + diurnal wind model
11 | 02:30 | 0 | 4996 | 0 | 0 | 0 | 0 | 2248 | 1998 | 🔴 REPR | Gaussian solar + diurnal wind model
12 | 02:45 | 0 | 4994 | 0 | 0 | 0 | 0 | 2247 | 1997 | 🔴 REPR | Gaussian solar + diurnal wind model
13 | 03:00 | 0 | 4993 | 0 | 0 | 0 | 0 | 2246 | 1997 | 🔴 REPR | Gaussian solar + diurnal wind model
14 | 03:15 | 0 | 4990 | 0 | 0 | 0 | 0 | 2245 | 1996 | 🔴 REPR | Gaussian solar + diurnal wind model
15 | 03:30 | 0 | 4988 | 0 | 0 | 0 | 0 | 2244 | 1995 | 🔴 REPR | Gaussian solar + diurnal wind model
16 | 03:45 | 0 | 4984 | 0 | 0 | 0 | 0 | 2242 | 1993 | 🔴 REPR | Gaussian solar + diurnal wind model
17 | 04:00 | 0 | 4980 | 0 | 0 | 0 | 0 | 2241 | 1992 | 🔴 REPR | Gaussian solar + diurnal wind model
18 | 04:15 | 0 | 4974 | 0 | 0 | 0 | 0 | 2238 | 1989 | 🔴 REPR | Gaussian solar + diurnal wind model
19 | 04:30 | 0 | 4967 | 0 | 0 | 0 | 0 | 2235 | 1986 | 🔴 REPR | Gaussian solar + diurnal wind model
20 | 04:45 | 0 | 4958 | 0 | 0 | 0 | 0 | 2231 | 1983 | 🔴 REPR | Gaussian solar + diurnal wind model
21 | 05:00 | 0 | 4948 | 0 | 0 | 0 | 0 | 2226 | 1979 | 🔴 REPR | Gaussian solar + diurnal wind model
22 | 05:15 | 0 | 4936 | 0 | 0 | 0 | 0 | 2221 | 1974 | 🔴 REPR | Gaussian solar + diurnal wind model
23 | 05:30 | 0 | 4920 | 0 | 0 | 0 | 0 | 2214 | 1968 | 🔴 REPR | Gaussian solar + diurnal wind model
24 | 05:45 | 0 | 4902 | 0 | 0 | 0 | 0 | 2205 | 1960 | 🔴 REPR | Gaussian solar + diurnal wind model
25 | 06:00 | 909 | 4881 | 163 | 318 | 227 | 201 | 2196 | 1952 | 🔴 REPR | Gaussian solar + diurnal wind model
26 | 06:15 | 1101 | 4856 | 198 | 385 | 275 | 243 | 2185 | 1942 | 🔴 REPR | Gaussian solar + diurnal wind model
27 | 06:30 | 1323 | 4827 | 238 | 463 | 330 | 292 | 2172 | 1930 | 🔴 REPR | Gaussian solar + diurnal wind model
28 | 06:45 | 1577 | 4794 | 283 | 551 | 394 | 349 | 2157 | 1917 | 🔴 REPR | Gaussian solar + diurnal wind model
29 | 07:00 | 1865 | 4756 | 335 | 652 | 466 | 412 | 2140 | 1902 | 🔴 REPR | Gaussian solar + diurnal wind model
30 | 07:15 | 2188 | 4713 | 393 | 765 | 547 | 483 | 2120 | 1885 | 🔴 REPR | Gaussian solar + diurnal wind model
31 | 07:30 | 2546 | 4664 | 458 | 891 | 636 | 561 | 2098 | 1865 | 🔴 REPR | Gaussian solar + diurnal wind model
32 | 07:45 | 2939 | 4610 | 529 | 1028 | 734 | 648 | 2074 | 1844 | 🔴 REPR | Gaussian solar + diurnal wind model
33 | 08:00 | 3367 | 4551 | 606 | 1178 | 841 | 742 | 2047 | 1820 | 🔴 REPR | Gaussian solar + diurnal wind model
34 | 08:15 | 3825 | 4486 | 688 | 1338 | 956 | 843 | 2018 | 1794 | 🔴 REPR | Gaussian solar + diurnal wind model
35 | 08:30 | 4312 | 4415 | 776 | 1509 | 1078 | 949 | 1986 | 1766 | 🔴 REPR | Gaussian solar + diurnal wind model
36 | 08:45 | 4822 | 4340 | 867 | 1687 | 1205 | 1063 | 1953 | 1736 | 🔴 REPR | Gaussian solar + diurnal wind model
37 | 09:00 | 5349 | 4259 | 962 | 1872 | 1337 | 1178 | 1916 | 1703 | 🔴 REPR | Gaussian solar + diurnal wind model
38 | 09:15 | 5887 | 4175 | 1059 | 2060 | 1471 | 1297 | 1878 | 1670 | 🔴 REPR | Gaussian solar + diurnal wind model
39 | 09:30 | 6428 | 4088 | 1157 | 2249 | 1607 | 1415 | 1839 | 1635 | 🔴 REPR | Gaussian solar + diurnal wind model
40 | 09:45 | 6963 | 3999 | 1253 | 2437 | 1740 | 1533 | 1799 | 1599 | 🔴 REPR | Gaussian solar + diurnal wind model
41 | 10:00 | 7482 | 3908 | 1346 | 2618 | 1870 | 1648 | 1758 | 1563 | 🔴 REPR | Gaussian solar + diurnal wind model
42 | 10:15 | 7976 | 3817 | 1435 | 2791 | 1994 | 1756 | 1717 | 1526 | 🔴 REPR | Gaussian solar + diurnal wind model
43 | 10:30 | 8435 | 3728 | 1518 | 2952 | 2108 | 1857 | 1677 | 1491 | 🔴 REPR | Gaussian solar + diurnal wind model
44 | 10:45 | 8850 | 3641 | 1593 | 3097 | 2212 | 1948 | 1638 | 1456 | 🔴 REPR | Gaussian solar + diurnal wind model
45 | 11:00 | 9211 | 3558 | 1657 | 3223 | 2302 | 2029 | 1601 | 1423 | 🔴 REPR | Gaussian solar + diurnal wind model
46 | 11:15 | 9511 | 3481 | 1711 | 3328 | 2377 | 2095 | 1566 | 1392 | 🔴 REPR | Gaussian solar + diurnal wind model
47 | 11:30 | 9743 | 3411 | 1753 | 3410 | 2435 | 2145 | 1534 | 1364 | 🔴 REPR | Gaussian solar + diurnal wind model
48 | 11:45 | 9901 | 3349 | 1782 | 3465 | 2475 | 2179 | 1507 | 1339 | 🔴 REPR | Gaussian solar + diurnal wind model
49 | 12:00 | 9982 | 3297 | 1796 | 3493 | 2495 | 2198 | 1483 | 1318 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
50 | 12:15 | 9983 | 3255 | 1796 | 3494 | 2495 | 2198 | 1464 | 1302 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
51 | 12:30 | 9906 | 3225 | 1783 | 3467 | 2476 | 2180 | 1451 | 1290 | 🔴 REPR | Gaussian solar + diurnal wind model
52 | 12:45 | 9750 | 3206 | 1755 | 3412 | 2437 | 2146 | 1442 | 1282 | 🔴 REPR | Gaussian solar + diurnal wind model
53 | 13:00 | 9522 | 3201 | 1713 | 3332 | 2380 | 2097 | 1440 | 1280 | 🔴 REPR | Gaussian solar + diurnal wind model
54 | 13:15 | 9224 | 3207 | 1660 | 3228 | 2306 | 2030 | 1443 | 1282 | 🔴 REPR | Gaussian solar + diurnal wind model
55 | 13:30 | 8865 | 3227 | 1595 | 3102 | 2216 | 1952 | 1452 | 1290 | 🔴 REPR | Gaussian solar + diurnal wind model
56 | 13:45 | 8452 | 3259 | 1521 | 2958 | 2113 | 1860 | 1466 | 1303 | 🔴 REPR | Gaussian solar + diurnal wind model
57 | 14:00 | 7995 | 3303 | 1439 | 2798 | 1998 | 1760 | 1486 | 1321 | 🔴 REPR | Gaussian solar + diurnal wind model
58 | 14:15 | 7502 | 3358 | 1350 | 2625 | 1875 | 1652 | 1511 | 1343 | 🔴 REPR | Gaussian solar + diurnal wind model
59 | 14:30 | 6984 | 3424 | 1257 | 2444 | 1746 | 1537 | 1540 | 1369 | 🔴 REPR | Gaussian solar + diurnal wind model
60 | 14:45 | 6450 | 3500 | 1161 | 2257 | 1612 | 1420 | 1575 | 1400 | 🔴 REPR | Gaussian solar + diurnal wind model
61 | 15:00 | 5909 | 3586 | 1063 | 2068 | 1477 | 1301 | 1613 | 1434 | 🔴 REPR | Gaussian solar + diurnal wind model
62 | 15:15 | 5371 | 3679 | 966 | 1879 | 1342 | 1184 | 1655 | 1471 | 🔴 REPR | Gaussian solar + diurnal wind model
63 | 15:30 | 4843 | 3780 | 871 | 1695 | 1210 | 1067 | 1701 | 1512 | 🔴 REPR | Gaussian solar + diurnal wind model
64 | 15:45 | 4332 | 3888 | 779 | 1516 | 1083 | 954 | 1749 | 1555 | 🔴 REPR | Gaussian solar + diurnal wind model
65 | 16:00 | 3844 | 4003 | 691 | 1345 | 961 | 847 | 1801 | 1601 | 🔴 REPR | Gaussian solar + diurnal wind model
66 | 16:15 | 3384 | 4124 | 609 | 1184 | 846 | 745 | 1855 | 1649 | 🔴 REPR | Gaussian solar + diurnal wind model
67 | 16:30 | 2956 | 4250 | 532 | 1034 | 739 | 651 | 1912 | 1700 | 🔴 REPR | Gaussian solar + diurnal wind model
68 | 16:45 | 2561 | 4382 | 460 | 896 | 640 | 565 | 1971 | 1752 | 🔴 REPR | Gaussian solar + diurnal wind model
69 | 17:00 | 2201 | 4519 | 396 | 770 | 550 | 485 | 2033 | 1807 | 🔴 REPR | Gaussian solar + diurnal wind model
70 | 17:15 | 1877 | 4660 | 337 | 656 | 469 | 415 | 2097 | 1864 | 🔴 REPR | Gaussian solar + diurnal wind model
71 | 17:30 | 1588 | 4805 | 285 | 555 | 397 | 351 | 2162 | 1922 | 🔴 REPR | Gaussian solar + diurnal wind model
72 | 17:45 | 1333 | 4952 | 239 | 466 | 333 | 295 | 2228 | 1980 | 🔴 REPR | Gaussian solar + diurnal wind model
73 | 18:00 | 1110 | 5100 | 199 | 388 | 277 | 246 | 2295 | 2040 | 🔴 REPR | Gaussian solar + diurnal wind model
74 | 18:15 | 916 | 5248 | 164 | 320 | 229 | 203 | 2361 | 2099 | 🔴 REPR | Gaussian solar + diurnal wind model
75 | 18:30 | 751 | 5392 | 135 | 262 | 187 | 167 | 2426 | 2156 | 🔴 REPR | Gaussian solar + diurnal wind model
76 | 18:45 | 0 | 5531 | 0 | 0 | 0 | 0 | 2488 | 2212 | 🔴 REPR | Gaussian solar + diurnal wind model
77 | 19:00 | 0 | 5662 | 0 | 0 | 0 | 0 | 2547 | 2264 | 🔴 REPR | Gaussian solar + diurnal wind model
78 | 19:15 | 0 | 5781 | 0 | 0 | 0 | 0 | 2601 | 2312 | 🔴 REPR | Gaussian solar + diurnal wind model
79 | 19:30 | 0 | 5886 | 0 | 0 | 0 | 0 | 2648 | 2354 | 🔴 REPR | Gaussian solar + diurnal wind model
80 | 19:45 | 0 | 5975 | 0 | 0 | 0 | 0 | 2688 | 2390 | 🔴 REPR | Gaussian solar + diurnal wind model
81 | 20:00 | 0 | 6044 | 0 | 0 | 0 | 0 | 2719 | 2417 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
82 | 20:15 | 0 | 6093 | 0 | 0 | 0 | 0 | 2741 | 2437 | 🟢 AUTH anchor | WRLDC PSP 30-May-2026
83 | 20:30 | 0 | 6120 | 0 | 0 | 0 | 0 | 2754 | 2448 | 🔴 REPR | Gaussian solar + diurnal wind model
84 | 20:45 | 0 | 6126 | 0 | 0 | 0 | 0 | 2756 | 2450 | 🔴 REPR | Gaussian solar + diurnal wind model
85 | 21:00 | 0 | 6111 | 0 | 0 | 0 | 0 | 2749 | 2444 | 🔴 REPR | Gaussian solar + diurnal wind model
86 | 21:15 | 0 | 6077 | 0 | 0 | 0 | 0 | 2734 | 2430 | 🔴 REPR | Gaussian solar + diurnal wind model
87 | 21:30 | 0 | 6026 | 0 | 0 | 0 | 0 | 2711 | 2410 | 🔴 REPR | Gaussian solar + diurnal wind model
88 | 21:45 | 0 | 5961 | 0 | 0 | 0 | 0 | 2682 | 2384 | 🔴 REPR | Gaussian solar + diurnal wind model
89 | 22:00 | 0 | 5885 | 0 | 0 | 0 | 0 | 2648 | 2354 | 🔴 REPR | Gaussian solar + diurnal wind model
90 | 22:15 | 0 | 5802 | 0 | 0 | 0 | 0 | 2610 | 2320 | 🔴 REPR | Gaussian solar + diurnal wind model
91 | 22:30 | 0 | 5715 | 0 | 0 | 0 | 0 | 2571 | 2286 | 🔴 REPR | Gaussian solar + diurnal wind model
92 | 22:45 | 0 | 5628 | 0 | 0 | 0 | 0 | 2532 | 2251 | 🔴 REPR | Gaussian solar + diurnal wind model
93 | 23:00 | 0 | 5542 | 0 | 0 | 0 | 0 | 2493 | 2216 | 🔴 REPR | Gaussian solar + diurnal wind model
94 | 23:15 | 0 | 5461 | 0 | 0 | 0 | 0 | 2457 | 2184 | 🔴 REPR | Gaussian solar + diurnal wind model
95 | 23:30 | 0 | 5385 | 0 | 0 | 0 | 0 | 2423 | 2154 | 🔴 REPR | Gaussian solar + diurnal wind model
96 | 23:45 | 0 | 5317 | 0 | 0 | 0 | 0 | 2392 | 2126 | 🔴 REPR | Gaussian solar + diurnal wind model

## 23_LINE_IMPEDANCES
TRANSMISSION LINE IMPEDANCES R/X/B ¦ 🟠 PROXY — Standard ACSR × map lengths ¦ MUST be replaced with GETCO actual data
DATA AUTHENTICITY: 🟢 AUTH = Official source / uploaded doc ¦ 🟡 DERIV = Calculated from authentic data ¦ 🟠 PROXY = Regulatory norm (CEA/CERC/IEA) — valid but not unit-specific ¦ 🔴 REPR = Reproduced by engineering judgment — MUST BE VERIFIED before GAMS use CALCULATION BASIS: 220kV ACSR Zebra: r=0.073 Ω/km, x=0.356 Ω/km, b=2.75μS/km, Smax=300 MVA/ckt. 400kV ACSR Moose: r=0.049 Ω/km, x=0.312 Ω/km, b=3.2μS/km, Smax=600 MVA/ckt. 765kV: r=0.025 Ω/km, x=0.265 Ω/km, b=3.6μS/km, Smax=2000 MVA/ckt. Base: 100 MVA. Zbase=kV²/100. R_pu=r_Ω/Zbase, X_pu=x_Ω/Zbase. Lengths from Sheet 14 (map estimates). HVDC modelled as power injection — R/X/B = 0.
LINE PARAMETERS — Per Unit on 100 MVA System Base
# | From Bus | To Bus | kV | Ckts | Length (km) | R_pu (100MVA) | X_pu (100MVA) | B_pu (100MVA) | Smax (MVA) | Data Type | Basis
1 | KANSARI | RANA PGCIL | 765 | 1 | 220 | 0.00094 | 0.009962 | 4.635 | 2000 | 🟠 PROXY | ACSR std params × 220km / 1ckt on 765kV
2 | KHAVDA-1 | BHUJ PGCIL | 765 | 2 | 120 | 0.000256 | 0.002717 | 5.0563 | 4000 | 🟠 PROXY | ACSR std params × 120km / 2ckt on 765kV
3 | KHAVDA-2 | KANSARI | 765 | 2 | 250 | 0.000534 | 0.00566 | 10.5341 | 4000 | 🟠 PROXY | ACSR std params × 250km / 2ckt on 765kV
4 | RANA | VADODARA | 765 | 1 | 120 | 0.000513 | 0.005434 | 2.5282 | 2000 | 🟠 PROXY | ACSR std params × 120km / 1ckt on 765kV
5 | KANSARI | CHITTORGARH NR | 765 | 2 | 280 | 0.000598 | 0.006339 | 11.7981 | 4000 | 🟠 PROXY | ACSR std params × 280km / 2ckt on 765kV
6 | MUNDRA HVDC | MOHINDARGARH NR | 500 | 1 | 900 | 0 | 0 | 0 | 1500 | 🔴 REPR | HVDC: model as power injection ±1500MW
7 | BHIMASAR | VANSANA | 400 | 2 | 80 | 0.001225 | 0.0078 | 0.8192 | 1200 | 🟠 PROXY | ACSR std params × 80km / 2ckt on 400kV
8 | BHIMASAR | BHUJ | 400 | 2 | 60 | 0.000919 | 0.00585 | 0.6144 | 1200 | 🟠 PROXY | ACSR std params × 60km / 2ckt on 400kV
9 | MUNDRA | BHIMASAR | 400 | 2 | 50 | 0.000766 | 0.004875 | 0.512 | 1200 | 🟠 PROXY | ACSR std params × 50km / 2ckt on 400kV
10 | VANSANA | HALVAD | 400 | 2 | 90 | 0.001378 | 0.008775 | 0.9216 | 1200 | 🟠 PROXY | ACSR std params × 90km / 2ckt on 400kV
11 | HALVAD | SURENDRANAGAR | 400 | 2 | 70 | 0.001072 | 0.006825 | 0.7168 | 1200 | 🟠 PROXY | ACSR std params × 70km / 2ckt on 400kV
12 | SURENDRANAGAR | RANASAN | 400 | 2 | 100 | 0.001531 | 0.00975 | 1.024 | 1200 | 🟠 PROXY | ACSR std params × 100km / 2ckt on 400kV
13 | JETPUR | RAJKOT | 400 | 2 | 35 | 0.000536 | 0.003413 | 0.3584 | 1200 | 🟠 PROXY | ACSR std params × 35km / 2ckt on 400kV
14 | JETPUR | AMRELI | 400 | 1 | 55 | 0.001684 | 0.010725 | 0.2816 | 600 | 🟠 PROXY | ACSR std params × 55km / 1ckt on 400kV
15 | JETPUR | BHAVNAGAR | 400 | 1 | 80 | 0.00245 | 0.0156 | 0.4096 | 600 | 🟠 PROXY | ACSR std params × 80km / 1ckt on 400kV
16 | DEHGAM | RANA | 400 | 2 | 30 | 0.000459 | 0.002925 | 0.3072 | 1200 | 🟠 PROXY | ACSR std params × 30km / 2ckt on 400kV
17 | DEHGAM | RANASAN | 400 | 2 | 40 | 0.000612 | 0.0039 | 0.4096 | 1200 | 🟠 PROXY | ACSR std params × 40km / 2ckt on 400kV
18 | RANASAN | WANAKBORI | 400 | 2 | 35 | 0.000536 | 0.003413 | 0.3584 | 1200 | 🟠 PROXY | ACSR std params × 35km / 2ckt on 400kV
19 | RANA | VADODARA PGCIL | 400 | 2 | 100 | 0.001531 | 0.00975 | 1.024 | 1200 | 🟠 PROXY | ACSR std params × 100km / 2ckt on 400kV
20 | VADODARA | KASOR | 400 | 2 | 15 | 0.00023 | 0.001462 | 0.1536 | 1200 | 🟠 PROXY | ACSR std params × 15km / 2ckt on 400kV
21 | KASOR | SURAT PGCIL | 400 | 2 | 90 | 0.001378 | 0.008775 | 0.9216 | 1200 | 🟠 PROXY | ACSR std params × 90km / 2ckt on 400kV
22 | SURAT | VALSAD | 400 | 2 | 60 | 0.000919 | 0.00585 | 0.6144 | 1200 | 🟠 PROXY | ACSR std params × 60km / 2ckt on 400kV
23 | VALSAD | MUMBAI PGCIL | 400 | 2 | 180 | 0.002756 | 0.01755 | 1.8432 | 1200 | 🟠 PROXY | ACSR std params × 180km / 2ckt on 400kV
24 | VADODARA | INDORE MP | 400 | 2 | 250 | 0.003828 | 0.024375 | 2.56 | 1200 | 🟠 PROXY | ACSR std params × 250km / 2ckt on 400kV
25 | BHIMASAR | AKRIMOTA | 220 | 2 | 60 | 0.004525 | 0.022066 | 0.15972 | 600 | 🟠 PROXY | ACSR std params × 60km / 2ckt on 220kV
26 | VANSANA | SIKKA | 220 | 2 | 70 | 0.005279 | 0.025744 | 0.18634 | 600 | 🟠 PROXY | ACSR std params × 70km / 2ckt on 220kV
27 | VANSANA | JAMNAGAR | 220 | 2 | 80 | 0.006033 | 0.029421 | 0.21296 | 600 | 🟠 PROXY | ACSR std params × 80km / 2ckt on 220kV
28 | VADINAR | SIKKA | 220 | 2 | 30 | 0.002262 | 0.011033 | 0.07986 | 600 | 🟠 PROXY | ACSR std params × 30km / 2ckt on 220kV
29 | SIKKA | JAMNAGAR | 220 | 2 | 25 | 0.001885 | 0.009194 | 0.06655 | 600 | 🟠 PROXY | ACSR std params × 25km / 2ckt on 220kV
30 | JAMNAGAR | RAJKOT | 220 | 2 | 90 | 0.006787 | 0.033099 | 0.23958 | 600 | 🟠 PROXY | ACSR std params × 90km / 2ckt on 220kV
31 | RAJKOT | MORBI | 220 | 2 | 60 | 0.004525 | 0.022066 | 0.15972 | 600 | 🟠 PROXY | ACSR std params × 60km / 2ckt on 220kV
32 | RAJKOT | WANKANER | 220 | 2 | 40 | 0.003017 | 0.014711 | 0.10648 | 600 | 🟠 PROXY | ACSR std params × 40km / 2ckt on 220kV
33 | JETPUR | JUNAGADH | 220 | 2 | 55 | 0.004148 | 0.020227 | 0.14641 | 600 | 🟠 PROXY | ACSR std params × 55km / 2ckt on 220kV
34 | AMRELI | BHAVNAGAR | 220 | 2 | 65 | 0.004902 | 0.023905 | 0.17303 | 600 | 🟠 PROXY | ACSR std params × 65km / 2ckt on 220kV
35 | PIPAVAV | AMRELI | 220 | 1 | 55 | 0.008295 | 0.040455 | 0.073205 | 300 | 🟠 PROXY | ACSR std params × 55km / 1ckt on 220kV
36 | MEHSANA | GANDHINAGAR | 220 | 4 | 30 | 0.001131 | 0.005517 | 0.15972 | 1200 | 🟠 PROXY | ACSR std params × 30km / 4ckt on 220kV
37 | BANASKANTHA | MEHSANA | 220 | 2 | 60 | 0.004525 | 0.022066 | 0.15972 | 600 | 🟠 PROXY | ACSR std params × 60km / 2ckt on 220kV
38 | SABARKANTHA | MEHSANA | 220 | 2 | 55 | 0.004148 | 0.020227 | 0.14641 | 600 | 🟠 PROXY | ACSR std params × 55km / 2ckt on 220kV
39 | PATAN | MEHSANA | 220 | 2 | 50 | 0.003771 | 0.018388 | 0.1331 | 600 | 🟠 PROXY | ACSR std params × 50km / 2ckt on 220kV
40 | KANSARI | MEHSANA | 220 | 2 | 80 | 0.006033 | 0.029421 | 0.21296 | 600 | 🟠 PROXY | ACSR std params × 80km / 2ckt on 220kV
41 | CHARANKA | PATAN | 220 | 4 | 60 | 0.002262 | 0.011033 | 0.31944 | 1200 | 🟠 PROXY | ACSR std params × 60km / 4ckt on 220kV
42 | GANDHINAGAR | WANAKBORI | 220 | 4 | 60 | 0.002262 | 0.011033 | 0.31944 | 1200 | 🟠 PROXY | ACSR std params × 60km / 4ckt on 220kV
43 | WANAKBORI | VADODARA | 220 | 4 | 65 | 0.002451 | 0.011952 | 0.34606 | 1200 | 🟠 PROXY | ACSR std params × 65km / 4ckt on 220kV
44 | WANAKBORI | KADANA | 220 | 2 | 50 | 0.003771 | 0.018388 | 0.1331 | 600 | 🟠 PROXY | ACSR std params × 50km / 2ckt on 220kV
45 | ANAND | VADODARA | 220 | 2 | 40 | 0.003017 | 0.014711 | 0.10648 | 600 | 🟠 PROXY | ACSR std params × 40km / 2ckt on 220kV
46 | DEHGAM | GANDHINAGAR | 220 | 4 | 15 | 0.000566 | 0.002758 | 0.07986 | 1200 | 🟠 PROXY | ACSR std params × 15km / 4ckt on 220kV
47 | UKAI TPS | SURAT | 220 | 4 | 60 | 0.002262 | 0.011033 | 0.31944 | 1200 | 🟠 PROXY | ACSR std params × 60km / 4ckt on 220kV
48 | UKAI TPS | VADODARA | 220 | 2 | 110 | 0.008295 | 0.040455 | 0.29282 | 600 | 🟠 PROXY | ACSR std params × 110km / 2ckt on 220kV
49 | SURAT | BHARUCH | 220 | 4 | 50 | 0.001885 | 0.009194 | 0.2662 | 1200 | 🟠 PROXY | ACSR std params × 50km / 4ckt on 220kV
50 | BHARUCH | VADODARA | 220 | 4 | 55 | 0.002074 | 0.010114 | 0.29282 | 1200 | 🟠 PROXY | ACSR std params × 55km / 4ckt on 220kV
51 | HAZIRA | SURAT | 220 | 2 | 15 | 0.001131 | 0.005517 | 0.03993 | 600 | 🟠 PROXY | ACSR std params × 15km / 2ckt on 220kV
52 | KAWAS | BHARUCH | 220 | 2 | 20 | 0.001508 | 0.007355 | 0.05324 | 600 | 🟠 PROXY | ACSR std params × 20km / 2ckt on 220kV
53 | JHANOR | BHARUCH | 220 | 2 | 25 | 0.001885 | 0.009194 | 0.06655 | 600 | 🟠 PROXY | ACSR std params × 25km / 2ckt on 220kV
54 | UTRAN | SURAT | 220 | 2 | 10 | 0.000754 | 0.003678 | 0.02662 | 600 | 🟠 PROXY | ACSR std params × 10km / 2ckt on 220kV
55 | SUGEN | SURAT | 220 | 2 | 15 | 0.001131 | 0.005517 | 0.03993 | 600 | 🟠 PROXY | ACSR std params × 15km / 2ckt on 220kV
56 | DHUVARAN | ANAND | 220 | 2 | 30 | 0.002262 | 0.011033 | 0.07986 | 600 | 🟠 PROXY | ACSR std params × 30km / 2ckt on 220kV
57 | SURAT | NAVSARI | 220 | 2 | 45 | 0.003394 | 0.01655 | 0.11979 | 600 | 🟠 PROXY | ACSR std params × 45km / 2ckt on 220kV
58 | NAVSARI | VALSAD | 220 | 2 | 35 | 0.002639 | 0.012872 | 0.09317 | 600 | 🟠 PROXY | ACSR std params × 35km / 2ckt on 220kV
59 | GODHRA | NAGDA MP | 220 | 2 | 180 | 0.013574 | 0.066198 | 0.47916 | 600 | 🟠 PROXY | ACSR std params × 180km / 2ckt on 220kV

## 24_STARTUP_COSTS
UNIT COMMITMENT PARAMETERS ¦ 🟠 PROXY + 🔴 REPR ¦ Derived from CERC tariff + CEA oil norms
DATA AUTHENTICITY: 🟢 AUTH = Official source / uploaded doc ¦ 🟡 DERIV = Calculated from authentic data ¦ 🟠 PROXY = Regulatory norm (CEA/CERC/IEA) — valid but not unit-specific ¦ 🔴 REPR = Reproduced by engineering judgment — MUST BE VERIFIED before GAMS use CALCULATION BASIS: No-load cost = Fixed charge (Rs/MW/hr from GERC tariff) × Pmin. Cold start cost = Pmin × MUT hrs × VC (Rs/kWh×1000) + Oil cost [5 kl/200MW × Rs65,000/kl × (Pmin/200)]. Warm = 50% of cold. Hot = 15% of cold. Fixed charge proxy: Subcritical coal Rs 250/MW/hr, SC coal Rs 200/MW/hr, Lignite Rs 240/MW/hr, Gas CCGT Rs 150/MW/hr. MUT/MDT from CEA norms (Sheet 16). Variable costs from merit order (Sheet 3). MUST VERIFY with GSECL/IPP.
UNIT COMMITMENT PARAMETERS — Gujarat Thermal Units
# | Station | Unit | Fuel | Inst (MW) | Pmin (MW) | VC (Rs/kWh) 🟢AUTH | Fixed Cost (Rs/MW/hr) 🟠PROXY | No-Load Cost(Rs/hr) 🟠PROXY | Cold Start (Rs) 🔴REPR | Warm Start (Rs) 🔴REPR | Hot Start (Rs) 🔴REPR | MUT (hr) 🟠PROXY | MDT (hr) 🟠PROXY
1 | GANDHINAGAR TPS | 3 | Coal | 210 | 141 | 5.39 | 250 | 35250 | 4789065 | 2394532 | 718360 | 6 | 4
2 | GANDHINAGAR TPS | 4 | Coal | 210 | 141 | 5.39 | 250 | 35250 | 4789065 | 2394532 | 718360 | 6 | 4
3 | GANDHINAGAR TPS | 5 | Coal | 210 | 154 | 5.18 | 250 | 38500 | 5036570 | 2518285 | 755486 | 6 | 4
4 | WANAKBORI TPS | 1 | Coal | 210 | 144.8 | 5.23 | 250 | 36200 | 4779124 | 2389562 | 716869 | 6 | 4
5 | WANAKBORI TPS | 2 | Coal | 210 | 144.8 | 5.23 | 250 | 36200 | 4779124 | 2389562 | 716869 | 6 | 4
6 | WANAKBORI TPS | 3 | Coal | 210 | 144.8 | 4.83 | 250 | 36200 | 4431604 | 2215802 | 664741 | 6 | 4
7 | WANAKBORI TPS | 4 | Coal | 210 | 144.8 | 5.23 | 250 | 36200 | 4779124 | 2389562 | 716869 | 6 | 4
8 | WANAKBORI TPS | 5 | Coal | 210 | 144.8 | 5.23 | 250 | 36200 | 4779124 | 2389562 | 716869 | 6 | 4
9 | WANAKBORI TPS | 6 | Coal | 210 | 144.8 | 5.23 | 250 | 36200 | 4779124 | 2389562 | 716869 | 6 | 4
10 | WANAKBORI TPS | 7 | Coal | 210 | 144.8 | 5.18 | 250 | 36200 | 4735684 | 2367842 | 710353 | 6 | 4
11 | UKAI TPS | 1 | Coal | 120 | 62 | 5.35 | 270 | 16740 | 2090950 | 1045475 | 313642 | 6 | 4
12 | UKAI TPS | 2 | Coal | 120 | 61.5 | 5.35 | 270 | 16605 | 2074088 | 1037044 | 311113 | 6 | 4
13 | UKAI TPS | 3 | Coal | 200 | 135 | 5.35 | 260 | 35100 | 4552875 | 2276438 | 682931 | 6 | 4
14 | UKAI TPS | 4 | Coal | 200 | 135 | 4.7 | 260 | 35100 | 4026375 | 2013188 | 603956 | 6 | 4
15 | UKAI TPS | 5 | Coal | 210 | 150.5 | 5.35 | 255 | 38378 | 5075612 | 2537806 | 761342 | 6 | 4
16 | UKAI TPS | 6 | Coal | 500 | 336.6 | 4.51 | 220 | 74052 | 12691503 | 6345752 | 1903725 | 8 | 6
17 | SIKKA TPS | 3 | Coal | 250 | 165 | 6.1 | 260 | 42900 | 6307125 | 3153562 | 946069 | 6 | 4
18 | SIKKA TPS | 4 | Coal | 250 | 165 | 6.1 | 260 | 42900 | 6307125 | 3153562 | 946069 | 6 | 4
19 | SLPP GIPCL | 1 | Lignite | 125 | 60 | 3.36 | 240 | 14400 | 1307100 | 653550 | 196065 | 6 | 4
20 | SLPP GIPCL | 2 | Lignite | 125 | 60 | 3.36 | 240 | 14400 | 1307100 | 653550 | 196065 | 6 | 4
21 | SLPP GIPCL | 3 | Lignite | 125 | 60 | 3.45 | 240 | 14400 | 1339500 | 669750 | 200925 | 6 | 4
22 | SLPP GIPCL | 4 | Lignite | 125 | 60 | 3.45 | 240 | 14400 | 1339500 | 669750 | 200925 | 6 | 4
23 | AKRIMOTA BECL | 1 | Lignite | 125 | 50 | 2.84 | 240 | 12000 | 933250 | 466625 | 139988 | 6 | 4
24 | AKRIMOTA BECL | 2 | Lignite | 125 | 50 | 2.84 | 240 | 12000 | 933250 | 466625 | 139988 | 6 | 4
25 | APL MUNDRA Stg1 | 1 | Coal | 330 | 200 | 5.16 | 200 | 40000 | 6517000 | 3258500 | 977550 | 6 | 4
26 | APL MUNDRA Stg1 | 2 | Coal | 330 | 200 | 5.16 | 200 | 40000 | 6517000 | 3258500 | 977550 | 6 | 4
27 | APL MUNDRA Stg1 | 3 | Coal | 330 | 200 | 5.16 | 200 | 40000 | 6517000 | 3258500 | 977550 | 6 | 4
28 | APL MUNDRA Stg1 | 4 | Coal | 330 | 200 | 5.17 | 200 | 40000 | 6529000 | 3264500 | 979350 | 6 | 4
29 | APL MUNDRA Stg2 | 1 | Coal | 660 | 400 | 4.82 | 185 | 74000 | 16074000 | 8037000 | 2411100 | 8 | 6
30 | APL MUNDRA Stg2 | 2 | Coal | 660 | 400 | 4.83 | 185 | 74000 | 16106000 | 8053000 | 2415900 | 8 | 6
31 | EPGL Essar | 1 | Coal | 600 | 360 | 5.52 | 188 | 67680 | 16482600 | 8241300 | 2472390 | 8 | 6
32 | EPGL Essar | 2 | Coal | 600 | 360 | 5.52 | 188 | 67680 | 16482600 | 8241300 | 2472390 | 8 | 6
33 | SUGEN CCPP | Block | Gas | 1148 | 30%×Inst | 4.94 | 150 | 51660 | 3962322 | 1981161 | 594348 | 2 | 2
34 | UNOSUGEN | Block | Gas | 383 | 30%×Inst | 3.79 | 150 | 17235 | 1057654 | 528827 | 158648 | 2 | 2
35 | DHUVARAN CCPP | Block | Gas | 595 | 30%×Inst | 13.08 | 160 | 28560 | 4959622 | 2479811 | 743943 | 2 | 2
36 | UTRAN CCPP | Block | Gas | 375 | 30%×Inst | 12.73 | 160 | 18000 | 3047062 | 1523531 | 457059 | 2 | 2

## 25_GAS_NOMINATIONS
GAS NOMINATION TIERS ¦ 🔴 REPR (volumes) + 🟢 AUTH (prices from merit order)
DATA AUTHENTICITY: 🟢 AUTH = Official source / uploaded doc ¦ 🟡 DERIV = Calculated from authentic data ¦ 🟠 PROXY = Regulatory norm (CEA/CERC/IEA) — valid but not unit-specific ¦ 🔴 REPR = Reproduced by engineering judgment — MUST BE VERIFIED before GAMS use THIS SHEET: Gas prices are 🟢 AUTH from SLDC Merit Order PDF (02-Jun-2026). Daily volumes REPRODUCED: APM/RLNG allocation estimated from plant PLF and PNGRB norms. Heat value assumed 8,500 kcal/SCM (typical Indian natural gas). HR assumed 1,900 kcal/kWh (CCGT). Volume = Pmin_MW × 24h × HR_kcal/kWh × 1000 / HV_kcal/SCM / 1e6 MMSCMD. ACTUAL volumes must come from GAIL/GSPC daily nominations.
GAS SUPPLY TIERS — All Gujarat Gas Plants
# | Plant | Owner | Cap (MW) | Tier | Gas Source | Price (Rs/kWh) 🟢AUTH | Daily Vol (MMSCMD) 🔴REPR | Active 30-May-26 | Merit Rank | Data Type | Note
1 | KAWAS NTPC | NTPC | 656.2 | APM | GAIL APM | 7.28 | 0.152 | No (0 MW) | 1 | 🟢AUTH price/🔴REPR vol | Central; Jhanor same tier
2 | KAWAS NTPC | NTPC | 656.2 | Non-APM | GAIL Non-APM | 7.42 | 0.152 | No | 2 | 🟢/🔴
3 | KAWAS NTPC | NTPC | 656.2 | RLNG | Long-term RLNG | 9.52 | 0.152 | No | 3 | 🟢/🔴
4 | KAWAS NTPC | NTPC | 656.2 | Comm.RLNG | Spot RLNG | 15.56 | 0.152 | No | 4 | 🟢/🔴
5 | KAWAS NTPC | NTPC | 656.2 | Liquid | LSHS/HSD | 25.11 | 0 | Emergency | 5 | 🟢/🔴 | Backup fuel
6 | JHANOR NTPC | NTPC | 657.4 | APM | GAIL APM | 7.25 | 0.153 | Limited | 1 | 🟢/🔴
7 | JHANOR NTPC | NTPC | 657.4 | Non-APM | GAIL Non-APM | 7.39 | 0.153 | No | 2 | 🟢/🔴
8 | JHANOR NTPC | NTPC | 657.4 | RLNG | Long-term RLNG | 10.04 | 0.153 | No | 3 | 🟢/🔴
9 | JHANOR NTPC | NTPC | 657.4 | Comm.RLNG | Spot RLNG | 15.69 | 0.153 | No | 4 | 🟢/🔴
10 | SUGEN Torrent | Torrent | 1148 | Contract | GSPC/GAIL | 4.94 | 0.267 | Yes 648MW | 1 | 🟢/🔴 | Active 30-May
11 | SUGEN Torrent | Torrent | 1148 | High Sea | Spot LNG Dahej | 10.3 | 0.267 | Minimal | 2 | 🟢/🔴
12 | SUGEN Torrent | Torrent | 1148 | GSPC Spot | GSPC | 15.1 | 0.267 | No | 3 | 🟢/🔴
13 | UNOSUGEN Torrent | Torrent | 383 | Must-run | GAIL/GSPC | 0 | 0.089 | Yes (must-run) | 0 | 🟢/🔴 | Must-run basis
14 | UNOSUGEN Torrent | Torrent | 383 | Contract | GSPC | 3.79 | 0.089 | Minimal | 1 | 🟢/🔴
15 | DHUVARAN-II GSECL | GSECL | 112 | Must-run | ONGC WO | 0 | 0.026 | Yes (must-run) | 0 | 🟢/🔴 | ONGC wellhead gas
16 | DHUVARAN-II GSECL | GSECL | 112 | High Sea | Spot LNG | 14.36 | 0.026 | No | 2 | 🟢/🔴
17 | DHUVARAN-II GSECL | GSECL | 112 | GSPC Spot | GSPC | 17.45 | 0.026 | No | 3 | 🟢/🔴
18 | DHUVARAN-III GSECL | GSECL | 376 | High Sea | Spot LNG | 13.08 | 0.087 | No | 2 | 🟢/🔴
19 | DHUVARAN-III GSECL | GSECL | 376 | GSPC Spot | GSPC | 15.1 | 0.087 | No | 3 | 🟢/🔴
20 | UTRAN GSECL | GSECL | 375 | High Sea | Spot LNG | 12.73 | 0.087 | No | 2 | 🟢/🔴
21 | UTRAN GSECL | GSECL | 375 | GSPC Spot | GSPC | 15.1 | 0.087 | No | 3 | 🟢/🔴
22 | GSEG GSPC | GSPC | 156 | High Sea | Spot LNG | 10.3 | 0.036 | No | 2 | 🟢/🔴
23 | GSEG GSPC | GSPC | 156 | GSPC Spot | GSPC | 15.1 | 0.036 | No | 3 | 🟢/🔴
24 | GPPC GSPC | GSPC | 703 | High Sea | Spot LNG | 11.89 | 0.163 | No | 2 | 🟢/🔴
25 | GPPC GSPC | GSPC | 703 | GSPC Spot | GSPC | 15.6 | 0.163 | No | 3 | 🟢/🔴